ANNEXURE-9

Scope for additional 33kV transmission line feeders if opted by bidder for only utilization of space  at PSS-2

- SCOPE

Space for future transmission lines panels are available at each 33 kV boards of PSS-2 at PEB-3 and PEB-4 as mentioned in the tender. It is to be noted that PSS-2 is under construction stage and expected to be ready by June-2025. The required details provided by Owner as per following shall be in a phased manner till June-2025. Bidder may opt for utilisation of this space subject to compliance of tentative specifications, GTPs, BOMs, GA Drawings and other details mentioned here under and subject to finalisation during detail Engineering.as  .

Owner will provide space  for use to install additional maximum 8 numbers of 33 kV Transmission line feeders. Tentative locations of these available spaces are indicated in “Annexure- 8 Tentative GA DRAWING OF 33KV PEB NUMBER 3 & 4 OF PSS-2”.

Manufacturing, supply, inspection, erection, testing for successful commissioning and O&M in all respect of these panels are (i.e. set of Breaker Panel-A and associated Metering Panel-B for each 33 kV transmission line) is in the scope of bidder.

Following tentative documents are part of this document.

| Sr | Description | Enclosed Document |
| --- | --- | --- |
| 1 | Tentative GTP of Main Breaker Panel and Associated Dedicated Metering Panel | Annexure 9a |
| 2 | Tentative GTP of ABT meter (Subject to approval from concerned competent authority) | Annexure 9b |
| 3 | Tentative Schematic of Main Breaker Panel. | Annexure 9c |
| 4 | Tentative Schematic of Associated Dedicated Metering Panel. | Annexure 9d |
| 5 | Tentative GA Drawing of Main Breaker Panel. | Annexure 9e |
| 6 | Tentative GA Drawing Associated Dedicated Metering Panel. | Annexure 9f |

- Scope of Owner

Following facilities are available at each Board of PEB-3 and PEB-4 of PSS-2 and will be extended by Owner to the successful bidder:

- Only Space for Main Breaker Panel and associated Dedicated Tariff Metering Panel in PEB-3 and PEB-4 (Maximum for 8 Nos of Transmission line feeders, however, use of adapter panel is not permitted).

- Ventilation System.

- Illumination system.

- Fire Alarm System

- CCTV systems.

- Earthing System.

- AC Auxiliary supply.

- DC Supply.

- UPS Supply.

- Cable Trench

- CMRI (Hand Held Data Collection Device) Equipment for ABT Meter

- Base Computer Software for ABT meters.

- Laptop with software's for ABT Meters.

- Breaker Trolley.

- Bus Side Earthing Trucks

- Cable Side Earthing Trucks

- Free ports (maximum 2 nos. for each Transmission line feeders/in each switchboard) on Ethernet switches (s) for SAS / SCADA communication

- Scope of 500MW EPC Contractor

Bidder has to supply breaker panel and metering panel for each TL bay identical in all respect to existing panels of PSS-2. Use of Adaptor panel is not permitted. Detail scope of supply and work is as under:

- Main Breaker panels (as per attached tentative GTP, GA and Scheme).

- Dedicated Tariff Metering Panel (as per attached tentative GTP, GA and Scheme).

- Frame and support system of Breaker panel and metering panels

- Main ABT meters (as per attached tentative GTP)

- Check ABT meters to be provided only if required by concerned competent statutory authority

- Approval for Main ABT Meter with Serial Number from concerned competent authority

- Laboratory and Site Testing of Main ABT Meter

- Laboratory and Site Testing of Tariff metering system instrument transformers as per requirement of concerned competent authority.

- Modems for ABT Meters (For Automated Metering Reading system)

- Inter panel DC supply wiring

- Inter panel AC auxiliary supply wiring

- Inter panel UPS supply wiring

- Power Quality Meter / Disturbance recorder (Integral Part of Breaker Panel-A) shall be same as that of existing panels of PSS-2.

- 33 kV Surge Arrestor (Integral Part of 33 kV Panels) shall be exactly same as that of existing panels of PSS-2

- Insulating Mats in front and rear side of the 33 kV Panels

- 33 KV Cable supply, installation, laying along with cable support system, cable sealing system (Multi Diameter type), cable termination kit (As per GIPCL approved make).

- All LT Power (if / wherever required) and control cables (If / wherever required) including all accessories.

- Communication Cabling / Wring (including terminations) for integration with SAS / CCMS (Centralized Control and Monitoring System) / SCADA system of followings equipment's / devices:

- ABT Meter:RS-485 Daisy chain with existing system (Dedicated Chain)

- Annunicator:RS-485 Daisy chain with existing system (Dedicated Chain)

- BCPU to ethernet switch (located in the same board) For each transmission line 2 nos. of ethernet ports shall be available. BPCU shall have two nos. of IEC 61850 communication ports for redundant communication with existing Substation Automation system (SAS) system. Relay programming shall be possible from existing SAS. BPCU shall be connected in fault tolerant ring configuration. Both relays shall support eRSTP protocol. Both relays shall have disturbance recording facility and send disturbance recording file to SAS on daily and event basis.  Post fault time required is 10 Sec, Pre-fault time is required 0.5 Sec @ Frequency of sampling is 1 kHz.

- DR-PQ Meter communication cabling with existing SAS system. over IEC 61850 and MODBUS RS 485 to Slave PPC. DR-PQ shall support minimum dual master. Ethernet switch is located on same Board.

- All communication wiring with same switchboard shall be inter panel wiring.

- Integration of all IED's with existing SAS / CMS / SCADA System with required software tags, licence etc.

- Integration with Energy Meters / MFM with existing Energy Management System with required software tags, licence etc.

- Annunciators shall be acknowledged from SAS.

- Cyber security compliance for Protection Relay, BPCU, DR-PQ, etc. Cyber security compliance shall be as per requirement of CEA Guidelines on Cyber Security in Power Sector 2021-1 & amendments, Information Technology Act, 2000 (21 of 2000) and National Cyber Security Policy, 2013 as amended from time to time, (NCIIPC) Guidelines and guidelines and advisories issued by Computer Emergency Response Team (CERT India). Bidder shall submit the required certificate/document as proof of cyber secured complied product.

- Cyber security audit of their entire PSS-2 Communication Infrastructure shall be conducted after commissioning through CERT-In empanelled Auditors so as to identify gaps and appropriate corrective actions shall be taken.

- Control Cable sealing system (shall be same as PSS-2 sealing system)

- Any other item or system mentioned or not but required for successful commissioning and operation is deemed in the scope of bidder.

- Foundation of the panel shall be same as existing PSS-2 33kV switchgear. Erecting the panels at allocated space with frame and support system of breaker panel and metering panel including required civil work in this regard.

- Required Cutting, welding of existing chequered plates and providing required chequered plates for uncovered area.

- Integration of Gas duct with existing panel board.

- Earthing of panels and any other earthing.

- Comprehensive Testing and commissioning of Panels

- Panels erection, testing and commissioning work shall be carried out without disturbing to existing system.

- EPC Contractor shall take utmost care while erection, testing and commissioning etc at PSS-2 existing system. However, in case of any unfortunate incident of damage to any existing system, it is sole responsibility of EPC contractor to re-instate the same immediately without any financially implication to the Owner.