VOLUME – II

PART – 3

SCOPE OF WORK & TECHNICAL SPECIFICATIONS

# TABLE OF CONTENTS

| Section | Description | PAGE NO. |
| --- | --- | --- |
|  | SCHEDULE-IV |  |
| ----- | List of Approved Manufacturers list | 4 |
|  | SCHEDULE-V |  |
| ----- | List of Spares For 3 Year O&M | 14 |
|  | SCHEDULE-VI |  |
|  | Procedure for Performance Guarantee (Pg) Testing | 27 |
| ----- | ANNEXURES |  |
| ANNEXURE - 1 | ELECTRICAL KEY SLD |  |
| ANNEXURE –2 | PRELIMINARY SCADA ARCHITECTURE |  |
| ANNEXURE –3 | SITE INVESTIGATION REPORT |  |
| ANNEXURE –4 | TYPICAL OVERALL PLANT LAYOUT (500 MW) WITH PERIPHERAL FENCING |  |
| ANNEXURE –5 | TYPICAL PVC COATED CHAIN LINK PERIPHERAL FENCE DETAILS |  |
| ANNEXURE –6 | TYPICAL CABLE TRAY PRECAST SUPPORT |  |
| ANNEXURE –7 | TENTATIVE OVERALL SINGLE LINE DIAGRAM OF 400/33KV GIS PSS-2 SUBSTATION |  |
| ANNEXURE –8 | TENTATIVE GA DRAWING OF 33KV PEB NUMBER 3 & 4 OF PSS-2 |  |
| ANNEXURE –9 | TENTATIVE SCOPE FOR ADDITIONAL 33KV TRANSMISSION LINE FEEDERS IF OPTED BY BIDDER FOR ONLY UTILIZATION OF SPACE AT PSS-2. |  |
| ANNEXURE –9a | TENTATIVE GTP OF MAIN BREAKER PANEL AND ASSOCIATED DEDICATED METERING PANEL |  |
| ANNEXURE –9b | TENTATIVE GTP OF ABT METER |  |
| ANNEXURE –9c | TENTATIVE SCHEMATIC OF MAIN BREAKER PANEL |  |
| ANNEXURE –9d | TENTATIVE SCHEMATIC OF ASSOCIATED DEDICATED METERING PANEL |  |
| ANNEXURE –9e | TENTATIVE GA DRAWING OF MAIN BREAKER PANEL |  |
| ANNEXURE –9f | TENTATIVE GA DRAWING ASSOCIATED DEDICATED METERING PANEL |  |
| ANNEXURE - 10 | TENTATIVE LAYOUT OF 400-33 KV PSS-2 |  |
| ANNEXURE 11 - | SIMPLIFIED CONCEPTUAL COMMUNICATION ARCHITECTURE 500MW |  |

# SCHEDULE – IV LIST OF APPROVED MANUFACTURERS

|  | Approved Vendor List |
| --- | --- |

| SL. No. | EQUIPMENT | VENDOR |
| --- | --- | --- |
|  | Inverters | - ABB (String & Central) - Sungrow - Ingeteam - SMA - TMEIC/ TOSHIBA - Schneider - Huawei (String) - Sineng |
|  | String Combiner Box | - Trinity Touch - ABB - Hensel |
|  | PV Connector | - Multi Contact - Amphenol - Bizzlink - Phoenix contact |
|  | Solar Cable | - Lapp - Leoni - Helukabel - Siechem - Apar - KEI - KEC |
|  | 33kV HV Cables | - KEI - Polycab - Torrent - KEC RPG cables - Universal - Apar - Gemscab - Sterlite - CCI |
|  | LV Cables | - KEI - Polycab - Torrent - KEC RPG cables - Universal - Apar - Gemscab - Sterlite - CCI - LAPP - NICCO |
|  | Inverter Duty Transformer | - Raychem - Shilchar - Toshiba - Danish - Schneider - VoltAmp - T&R - CGL - ABB - Sudhir Power |
|  | MCCB/ MCB/ ELCB/ RCBO/RCCB | - Siemens - ABB - Schneider - Merlin Gerin - GE AREVA - EATON - Allen Bradly |
| - 13. | HT switchgear & panel (33kV) | - ABB - Siemens - Schneider - GE - L&T - BHEL (Bhopal) |
| - 15. | L T Switchgear Panel, Control Panel, ACDB, DCDB, Annunciation Panel | - L&T - ABB - Siemens - Legrand - GE - Schneider - Trisquare - Technocraft - Sterling - Ohm energy management system private limited (Chennai) |
|  | Transformer Oil | - Apar - Savita - Raj petro - Shell eastern petroleum limited |
| - 17. | Auxiliary Transformers (Dry type, Oil Type and HT and LT) | - KAPPA - Voltech - TESLA - DANISH - CGL - Voltamp - Bharat BIJLEE - ABB - Inverter OEM Approved make(for Dry type only) - Kalpa Electrikal |
| - 18. | UPS | - Vertiv (previously known as Emerson) - ABB - Hitachi Hirel - Fuji Electric ConsulNeowatt private limited - EATON |
| - 20. | Battery Lead-Acid | - Exide |
| - 21. | Battery Charger | - Amararaja - Caldyne - HBL - Statcon - Dubas - Chhabi - Vertiv (previously known as Emerson) - Chloride / Exide - Hitahchi - HI-REL - Mass-Tech Control - Hoppecke Batterien - GMBH & CO KG - Saft india |
| - 22. | ESE Type Lightning Arrestor | - Jeff Techno Solution - Storm master - OBLUM - LAMCO - GE - CGL - ELPRO - Sabo System - Indelec Prevectron - Nimbus - Dmsgi |
| - 24. | Earthing Rod & Back filling compound | - Ashlok - ERICO - JEF Techno |
| - 25. | SCADA | - ABB - Rockwell - Siemens - Schneider - Honeywell - Emerson automation solution intelligent platforms - Phoenix Contact Electronics GmbH (Germany) |
| - 26. | PPC Controller with IOs | - ABB, - Siemens, - Schneider |
| - 27. | Computers and Printers | - DELL - HP - Canon - Ricoh HP - Brother - Advantech - Technics Infosol - Portwell-Laxsons - Avhis Technologies |
| - 28. | Fibre Optic Cable | - Helukabel - Lapp - KEC - RPG - Finolex - KEI - HFCL - Sterlite - Aksh,Apar - M/S Birla Cables - R & M - Molex, - Corning |
| - 29. | CCTV System | - Honeywell - Hikvision - Bosch - Pelco - Axis |
| - 30. | HVAC System / Split AC | - BlueStar - Voltas - Carrier - Daikan - O’General - Mitshubisi Heavy |
| - 31. | Lighting Fixtures | - Philips - CGL - Bajaj - Wipro - Havells |
| - 32. | DC Fuses | - Cooper Bussmann - Mersen - GE - Trinity Touch |
| - 33. | Surge Protection Devices (for Solar system) | - ABB - Citel - DEHNguard - Ferraz - Shawmut - Phoenix Contact |
| - 34. | 33kV termination Kit & Straight through joints | - Raychem RPG |
| - 35. | Protection Relays | - ABB - Schneider - GE (Alstom) - Siemens |
| - 36. | Tariff Meters (ABT Meter) | - Secure |
| - 37. | Electronic Digital Meters (A/V/pf/Hz./KWh) | - ABB - Conzerv - L&T - Automatic Electric - Rishabh - Secure - Schneider - Siemens |
| - 38. | Control Cables | - Polycab, - Apar, - Ravin, - Universal, - KEC RPG, - KEI, - Gloster, - Finolex, - SIECHEM,dynamic, - LAPP - RR cables |
| - 39. | Cable Glands, PVC shroud and Lugs | - Comet - Jainson - Dowell - 3D |
| - 40. | Polyamid Gland | - Hensel - Trinity Touch - Supa Flex Pvt. Ltd - Ortac |
| - 43. | Fire & Alarm System | - Honeywell - Siemens - UK,Edward - Autronica - Schrack |
| - 45. | Pyranometer | - Kipp & Zonnen (SMP11) |
|  | Albedometer | - Kipp & Zonnen |
| - 46. | Wind Sensor | - Theisclima - Met One Inc - NRG System - Thies Clima |
| - 47. | Wind Direction (WMS) | - NRG System - Thies Clima |
| - 48. | Rainfall Sensor | - NRG System - Thies Clima |
| - 49. | Ambient temperature sensor | - Campbell Scientific |
| - 50. | Module temperature sensor | - Campbell Scientific |
| - 51. | Soiling Station | - Campbell Scientific - Kipp & Zonnen |
| - 52. | WMS Data logger | - Campbell Scientific - NRG System |
|  | Occupancy Sensor | - Honeywell - Schneider - Bajaj |
| - 53. | Cement | - Ultratech - Dalmia - Ramco - ACC - Ambuja - Birala Gold - Sanghi - JK Lakshmi - Siddhi - Hathi - Hi-Bond - JSW cement - Nuvoco |
| - 54. | Admixtures / Water proofing compounds / Hardener | - Dr. Fixit - Sika - Fosroc |
| - 55. | Reinforcement Steel (CRS Fe 550D)_ | - TATA - Jindal - SAIL - RINL - Electrotherm |
| - 56. | Structural Steel | - JSW - TATA - Essar - Jindal - SAIL - RINL |
| - 57. | Aluminum Section for Door / Window / Partition | - Hindalco - Banco - Jindal |
| - 60. | Vitrified tiles/ Ceramic tiles-premium class | - Nitco - Kajaria - Asian - RAK - Somany - Johnson |
| - 61. | Acid resistant tiles | - Johnson - Kajaria - Somany |
| - 62. | Glass | - Saint-Gibain - Modi Glass - ASHAI India |
| - 66. | Acrylic and emulsion paint, weather proofing paint | - Asian - Indigo - Berger - Nerolac |
| - 67. | Putty | - Birla - Asian - Berger - Nerolac |
| - 68. | Acid /epoxy resistant paint | - Fosroc - Jotun |
| - 69. | Fireproof Sealant | - Sika - Fosroc - Hilti |
| - 70. | Non Shrink grout | - Sika - Fosroc - BASF - Pidilite |
| - 73. | False ceiling (Gypsum or Fiberglass board) | - Armstrong - saint Gobain |
|  | 33KV Surge Arrester | - Oblum - Elpro - Raychem - Lamco |

Note:

- The final make selected out of the recommended makes listed above shall be subject to the Owner’s approval during detailed Engineering.

- Wherever the make is not specified for any items, the Bidder shall submit credential for vendors for relevant items / equipment, out of which Owner shall decide acceptance of vendor based on review of credentials. This shall have no price implication. Owner reserves the right to reject the proposed vendor without assigning any reason.

- Bidder may suggest /request for approval of Additional vendor with credentials. Owner after review and verification, may consider the request of proposed additional vendor without any commitment and subject to overall vendor review with respect to tender specification requirements, vendor capability etc. Further owner reserves the right to reject the proposed vendor without assigning any reason.

- It is to be noted that no time extension for completion of project will be granted on account of request for vendor(s) approval.

# SCHEDULE – V LIST OF SPARES FOR 3 YEAR O&M

- Recommended Maintenance Tools and Tackles

  - Bidders shall furnish a list of recommended Maintenance Tools and Tackles which the Bidder considers necessary for the complete plant including those necessary during the O&M period. The Bidder shall maintain the tools and tackles as well as fault locating equipment during the complete O&M period. At the end of contracted O&M period, Bidder shall hand over all the tools and Tackles to GIPCL

  - The Bidder shall provide technically suitable tools and tackles for installation and erection of plant conforming to relevant BIS safety and technical standards for proper execution of work. Owner, in no way, shall be responsible for supply of any tools and tackles for implementation of the work and to carry out operation and maintenance activities.

  - One set of all special tools shall be furnished with each piece of equipment for dismantling, maintenance, adjustment, and calibration of the equipment. The tools shall be shipped in separate heavily constructed wooden boxes provided with hinged covers and padlock.

|  | List of Mandatory Spares |
| --- | --- |

  - The Bidder shall maintain an on-site inventory of the mandatory spares as listed below for smooth operation of the solar PV power plant. Mandatory spares are spares which are considered mandatory for trouble free operation of the plant and shall be maintained by the successful Bidder during the complete O&M period of three (3) years.

  - The quantity mentioned in column Total Quantity shall be considered as the sum of each type and each make, same shall be supplied in proportion to the total supplied quantity.

| SL. No. | ITEM / EQUIPMENT | Unit |  | Total Quantity | Description |
| --- | --- | --- | --- | --- | --- |
|  | SOLAR PV YARD |  |  |  |  |
|  | PV Connectors pair (Each Type) | Nos. |  | 500 | For PV Module inter Connections and String Wiring |
|  | Y- connectors pair | Nos. |  | 500 | - |
|  | String Combiner box (Each type) | Nos. |  |  |  |
|  | String Combiner Box (Complete Assembly) | Nos. |  | 10 |  |
|  | - Fuses -Outgoing (Each Type & rating) | Nos. |  | 200 | - |
|  | - Fuses - String (Each Type & rating) | Nos. |  | 1000 |  |
|  | - Isolator | Nos. |  | 10 | - |
|  | - Surge Arrestor / SPD (DC) | Nos. |  | 100 | - |
|  | MMS – complete set (In Loose condition) | Set |  | 5 | - |
|  | MMS-Fastener, Each Type | Sets |  | 50 |  |
|  | Fastener for Mounting Solar Panel | Sets |  | 1000 |  |
|  | Inverter (String Inverter, If applicable) | Lot |  | For 2 MW |  |
|  | Inverter (For Central Inverter, If applicable) |  |  |  |  |
|  | - Inverter (One Complete Set) for Each Type / Each Rating / Each Make (Ready to replace condition / Interchangeable) | Nos. |  | 1 |  |
|  | - IGBT Power Stack | Nos. |  | 20 | - |
|  | - Negative Grounding Fuses | Nos. |  | 50 | - |
|  | - Air Filter Set | Nos. |  | 50 | - |
|  | - DC contactor | Nos |  | 5 |  |
|  | - AC Contactor | Nos |  | 5 |  |
|  | - Air Circuit breaker | Nos |  | 2 |  |
|  | - Parts of Air Circuit breaker |  |  |  |  |
|  | - Closing Coil | Nos |  | 6 |  |
|  | - Tripping coil | Nos |  | 6 |  |
|  | - Spring charging motors | Nos |  | 6 |  |
|  | - Aux. Contact Block | Nos |  | 6 |  |
|  | - Set of Main Contacts | Sets |  | 3 |  |
|  | - Set of Fix Contacts | Sets |  | 3 |  |
|  | - Electronic protection unit of Breaker | Nos |  | 3 |  |
|  | - DC Surge Protector | Nos |  | 5 |  |
|  | - AC Surge Protector | Nos |  | 5 |  |
|  | - Cooling fan | Nos |  | 5 |  |
|  | - Inverter Fuses, | Nos |  | 48 |  |
|  | - Electronics Modules/ Card/ Display | Nos |  | 10 |  |
|  | - Current Transformer (or Sensor) /Voltage Transformer (or Sensor) | No |  | 10 |  |
|  | - Connectors/FRC cable | Set |  | 10 |  |
|  | - Aux AC/ DC Relays | Set |  | 10 |  |
|  | - Aux Transformer for Fan | No |  | 5 |  |
|  | DC Solar Cables and Jointing Kits |  |  |  |  |
|  | - string cable | Mtrs. |  | 5000 |  |
|  | - DC Power Cables- SCB to Inverter | Mtrs. |  | 1000 |  |
|  | - DC Power Cable Straight through Joint Kits, Each Size | Nos |  | 10 |  |
|  | - DC Power Cable Lugs / termination kits for End termination. | Nos |  | 15 |  |
|  | ESE LA Surge Counter | Nos. |  | 5 | - |
|  | ELECTRICAL SYSTEM SPARES |  |  |  |  |
|  | Inverter Transformers ( Items of Each type, Each Rating, Each make.) |  |  |  |  |
|  | - Complete winding Temperature Indicating equipment (WTI) with capillary temperature sensor | Nos. |  | 2 | - |
|  | - Oil temperature indicator with capillary temperature sensor | Nos. |  | 2 | - |
|  | - CT of each type | Nos. |  | 6 | - |
|  | - Transformer oil | Drum |  | 20 | - |
|  | - Silica Gel Breather | Nos. |  | 2 | - |
|  | - Pressure relief device with drain arrangement | Nos. |  | 2 | - |
|  | - Set of valves | Nos. |  | 2 | - |
|  | - Buchholz relay | Nos. |  | 2 | - |
|  | - HV bushing | Nos. |  | 6 | - |
|  | - LV bushing | Nos. |  | 18 | - |
|  | - Oil level gauge | Nos. |  | 2 | - |
|  | - Magnetic oil Gauge | Nos. |  | 2 | - |
|  | - Gasket set | Nos. |  | 1 |  |
|  | - Air cell | Nos. |  | 1 |  |
|  | - Prismatic Oil Level Gauge (POG) assembly | Sets |  | 2 |  |
|  | - remote indication of each type and rating for WTI & OTI | Sets |  | 2 |  |
|  | - WTI CT of each type and rating | set |  | 2 |  |
|  | - Gas Collection Device assembly | Sets |  | 2 |  |
|  | - Tap changer contacts | Nos |  | 2 |  |
|  | - Neutral Bushing | Nos |  | 2 |  |
|  | - Shield bushing | Nos |  | 4 |  |
|  | - Earthing support insulator (if equipped) | Nos |  | 4 |  |
|  | - CCU | Nos |  | 8 |  |
|  | - HV Cable box Disconnecting link | Set |  | 1 |  |
|  | - LV Cable box Disconnecting link | Set |  | 3 |  |
|  | - Insulators | Nos |  | 6 |  |
|  | - Bus bars | Nos |  | 2 |  |
|  | Dry type Auxiliary Transformers | Nos |  | 4 |  |
|  | 33kV Switchgear (Items of Each type, Each Rating, Each make.) |  |  |  |  |
|  | - 33KV breaker (Sub pooling Station) | Nos. |  | 2 | - |
|  | - 33KV Transmission line breaker | Nos |  | 1 | - |
|  | - ICOG Breaker (to be supplied only if diff than item no a) 33KV IDT breaker) | Nos |  | 2 | - |
|  | - Breaker complete set with operating mechanism and truck mounted | Nos. |  | 2 | - |
|  | - Closing Coil | Nos |  | 6 | - |
|  | - Tripping Coil | Nos |  | 6 | - |
|  | - Spring Charging Motors | Nos |  | 6 | - |
|  | - Aux. Contact Block | Nos |  | 6 | - |
|  | - Set of Main Contacts | Sets |  | 3 | - |
|  | - Set of Fix Contacts | Sets |  | 3 | - |
|  | - Bus bar | Sets |  | 1 |  |
|  | - Bus bar support insulators | Nos. |  | 12 | - |
|  | - Aux. switch assembly, limit position switches, Local/Remote selector switch, breaker control switches ammeter selector switch, voltmeter selector switch | Nos. |  | 2 | - |
|  | - Numerical Relays of each type used | Nos. |  | 10% | - |
|  | - Clustered type LED | Nos. |  | 10 | - |
|  | - CTs | Set |  | 3 | - |
|  | - VTs | Set |  | 3 | - |
|  | - MFM Meters | Nos. |  | 3 | - |
|  | - Fuses /MCBs | Nos. |  | 10% or min. 2 No. | - |
|  | - Surge Arrestor | Nos. |  | 3 | - |
|  | - VT Fuse | Nos. |  | 3 |  |
|  | - Limit Switch for spring charging indication | Nos |  | 5 |  |
|  | - Aux Contactors | Nos |  | 10 |  |
|  | - Aux Switch Block | Nos |  | 4 |  |
|  | - 33KV AL XLPE Armored Cable of Transmission line | Mtrs. |  | 2000 |  |
|  | - 33KV cable from IDT to 33KV sub pooling switchgear | Mtrs. |  | 1000 |  |
|  | - Termination Kit for 33KV AL XLPE Armored Cable of Transmission line | Nos. |  | 10 |  |
|  | - Termination Kit for 33KV cable from IDT to 33KV sub pooling switchgear | Nos. |  | 20 |  |
|  | - Jointing Kit for 33KV AL XLPE Armored Cable of Transmission line | Nos. |  | 10 |  |
|  | - Jointing Kit for 33KV cable from IDT to 33KV sub pooling switchgear | Nos. |  | 20 |  |
|  | - Annunciator | Nos |  | 04 |  |
|  | - Earthing Switch | Nos |  | 03 |  |
|  | - TTB (For meters) | Nos |  | 02 |  |
|  | - RTB (For relays) | Nos |  | 02 |  |
|  | - Trolley for Transmission line breaker | Nos |  | 02 |  |
|  | - Trolley for sub pooling breaker | Nos |  | 02 |  |
|  | - Hooter | Nos |  | 02 |  |
|  | - Space Heater, Thermostat, Door switch, Panel Handles, Hinges of each type | Nos |  | 02 |  |
|  | - Trip Circuit Supervision Relay for Breaker | No |  | 4 |  |
|  | - Trip Circuit Supervision Relay for Master Trip Relay | No |  | 4 |  |
|  | - DC Failure, AC Failure, Fuse Failure relay Auxxilary relays | Set |  | 3 |  |
|  | - Communication Probes / wires / connectors of each type for numerical relay | Set |  | 2 |  |
|  | - Gear box assembly for Spring Charging motor | Set |  | 5% (Minimum 2 Nos) |  |
|  | - Panel hardware accessories like Gasket, Knobs, Door Locks, Handle, Hinges, filter, Power Terminal Block shroud, breaker shroud/shutters, etc. | Set |  | 4 |  |
|  | LT System (Items of Each type, Each Rating, Each make.) |  |  |  |  |
|  | - MCCB (Complete set with handle, barrier, shroud etc.) | Nos |  | 6 | - |
|  | - MCBs and MPCBs | Nos |  | 5 | - |
|  | - Contactor | Nos |  | 06 | - |
|  | - Timer | Nos |  | 06 | - |
|  | - MFM | Nos |  | 02 | - |
|  | - Indicating Lamp & Push Buttons | Nos |  | 10 | - |
|  | - Bus bar | set |  | 1 |  |
|  | - Insulators | Nos |  | 3 |  |
|  | Lighting System (Items of Each type, Each Rating, Each make.) |  |  |  |  |
|  | - Lighting fixtures | Nos. |  | 5% | - |
|  | - Fuses/MCBs, contactors, auxiliary relays. Switches push buttons | Nos. |  | 10% | - |
|  | - Occupancy Sensor | Lot |  | 10% |  |
|  | - Modular Switch board plates, switches sockets, boxes, fan regulator (if applicable), RJ45, Blanks etc. | Lot |  | 10% |  |
|  | - Lighting Distribution board components like MCBs, RCCBs, ELCBs, contactors, Power Switches, Control Switches, Fuse, Terminal Block, timers etc | Lot |  | 10% |  |
|  | Battery System (Items of Each type, Each Rating, Each make.) |  |  |  |  |
|  | - SMPS for sub pooling station chargers | Nos |  | 02 | - |
|  | - MCCB | Nos. |  | 2 | - |
|  | - Fuses /MCB | Set |  | 5 | - |
|  | - Indicating Metering Instrument | Set |  | 2 | - |
|  | - Dry Battery Cell | Set |  | 20 | - |
|  | - Inter Cell connector, Complete set for 1 battery bank with nut, bolt and washer | Set |  | 1 | - |
|  | - Inter Row connector, Complete set for 1 battery bank with nut, bolt and washer | Set |  | 1 | - |
|  | - SAN Container of Battery Bank with top cover (Empty) | Set |  | 5 | - |
|  | - Vent Plugs | Nos |  | 20 | - |
|  | - Electrolyte for 1 battery Bank | Nos |  | 1 |  |
|  | - Hydrometer | Nos |  | 4 |  |
|  | - Hand gloves | Set |  | 2 |  |
|  | - Aux. Contactors | Nos |  | 2 |  |
|  | - Transducers | Nos |  | 2 |  |
|  | Aux. Transformers (Oil filled) (Items of Each type, Each Rating, Each make.) |  |  |  |  |
|  | - Complete winding Temperature Indicating equipment (WTI) with capillaries and temp. sensor | Nos. |  | 1 | - |
|  | - Oil temperature indicator with capillaries and temp. sensor | Nos. |  | 1 | - |
|  | - CT of each type | Nos. |  | 1 | - |
|  | - Transformer oil | Drum |  | 2 | - |
|  | - Silica Gel Breather | Nos. |  | 1 | - |
|  | - Pressure relief device | Nos. |  | 1 | - |
|  | - Valves | Set |  | 1 | - |
|  | - Buchholz relay | Nos. |  | 1 | - |
|  | - HV bushing | Nos. |  | 2 | - |
|  | - LV bushing | Nos. | 2 |  | - |
|  | - Neutral LV bushing | No | 1 |  |  |
|  | - Neutral HV bushing ( If applicable) | No | 1 |  |  |
|  | - Oil level gauge | Nos. | 1 |  | - |
|  | - Magnetic oil Gauge | Nos. | 1 |  | - |
|  | - Gasket set | Nos. | 1 |  |  |
|  | - Prismatic Oil Level Gauge (POG) assembly | Sets | 1 |  |  |
|  | - remote indication of each type and rating for WTI & OTI | Sets | 1 |  |  |
|  | - WTI CT | set | 1 |  |  |
|  | - Gas Collection Device assembly | Sets | 1 |  |  |
|  | - Tap changer contacts | Nos | 2 |  |  |
|  | INSTRUMENTATION AND CONTROL SYSTEMS SPARES |  |  |  |  |
|  | SCADA & PPC |  |  |  |  |
|  | Power Supply modules / Cards | Nos. |  | 2 | - |
|  | - I/O Cards (Each Type) | Nos. |  | 5% | - |
|  | - Network Cards /Ethernet Switches (Each Type) | Nos. |  | 5% | - |
|  | - Communication system spares of each type | Nos. |  | 5% | - |
|  | - Data Bus Cable of each type | Nos. |  | 3% | - |
|  | - Main Data Bus and Data Bus Controller | Nos. |  | 3% | - |
|  | - Fiber Optic Cable Converter/De-converter Unit (applicable if remote I/O module is supplied) | Nos. |  | 3% | - |
|  | - Connecting cable (any FRC, OFC Patch Cord) and plugs | Nos. |  | 3% | - |
|  | - Firewall | Nos |  | 1 | - |
|  | - Each Type of Electronics card for PPC system | No |  | 1 | - |
|  | - All other electronic modules | Nos. |  | 3% | - |
|  | - All type of converter (RS-232 to RS-485, RS-232 to Ethernet, RS-485 to Ethernet, RS-485 to Optical) each type | Nos |  | 3% | - |
|  | - Communication SPD for RS-485, Each Type | Nos |  | 3% | - |
|  | - Ethernet CAT6 (outdoor duty) | Rm |  | 100 | - |
|  | - RS 485 Cable Armored | Rm |  | 100 | - |
|  | - Lugs & glands -Various Sizes | Lum Sum |  | 1 Lot | - |
|  | - CCTV |  |  |  |  |
|  | Camera with power supply, Ethernet Switch | Nos. |  | 1 of each kind as complete unit | - |
|  | - Power supply adaptor for CCTV and Media Convertor | Nos. |  | 5 | For each Type of Power Supply requirement |
|  | - Cable for Power Supply of CCTV | Mtr |  | 100 |  |
|  | - WEATHER MONITORING STATION |  |  |  |  |
|  | Pyranometer | Nos. |  | 01 | - |
|  | - SMPS of data logger | Nos |  | 1 |  |
|  | - Each Type of Electronics Card | Nos |  | 1 |  |
|  | - FIBRE OPTIC CABLE |  |  |  |  |
|  | Fiber Optic cable | Mtrs. |  | 100 | - |
|  | - UPS |  |  |  |  |
|  | Electronics Cards/Displays, Each Type | No |  | 1 | In case of UPS of different type/ rating, Spares to be managed for each type/rating. |
|  | Capacitor, Each Type | No |  | 1 |  |
|  | Contactor/Relay, Each Type | No |  | 1 |  |
|  | Cooling Fan, Each Type | No |  | 3 |  |
|  | IGBT/ Thyristor/SCR, Each Type | Set |  | 1 |  |
|  | Fuse, Each Rating | Set |  | 1 |  |
|  | Robotic Module Cleaning System |  |  |  |  |
|  | Robot | Nos |  | 10 |  |
|  | Electronic Cards/Controller Module, Each type | Nos |  | 20 |  |
|  | Sensor, Each Type | Nos |  | 20 |  |
|  | Mop/Brush | Nos |  | 100 |  |
|  | Bearing/Roller/Wheels | Nos |  | 50 |  |
|  | Tracker |  |  |  |  |
|  | Tracking Motor /Hyd system assembly | Nos |  | 10 |  |
|  | Electronic Cards, Each type | Nos |  | 5 |  |
|  | Sensor/ limit switch Each Type | Nos |  | 5 |  |
|  | Battery (Each type, rating and make) | Nos |  | 20 |  |
|  | Charging Module | Nos |  | 10 |  |
|  | Module Cleaning System |  |  |  |  |
|  | Each Type of Pipe | Mtr |  | 100 |  |
|  | Elbow, Tee and Coupling, Each Size | Nos |  | 50 |  |
|  | Isolation Valve, Each Size | Nos |  | 50 |  |
|  | Electric Motor & Pump | Set |  | 02 |  |
|  | Fire Alarm Systems |  |  |  |  |
|  | Electronic Modules, Each Type | Nos |  | 2 |  |
|  | Fire Detector, MCP, Each Type | Nos |  | 20 |  |
|  | Hooter | Nos |  | 3 |  |
|  | Ventilation system (HVAC) |  |  |  |  |
|  | Drive Motor | No |  | 1 |  |
|  | Blower with Shaft and bearings etc. | Set |  | 1 |  |
|  | Panel type air pre-filter for complete AHU system | Set |  | 1 |  |
|  | Spare for AHU Electrical panel like , Aux. relays, protective relays, Auxiliary Contactors, Main Contactor, Power MCB / MCCB, Power Switch/ SFU, Push Buttons, Control Switches, Indicating Lamps, Annunciator, Control MCB, Control Fuses with carrier base and links, Timers, Power and Control Terminal Blocks etc. of each type & rating | Set |  | 1 |  |
|  | List of Special Tools and Tackles as per clause no. 1.1 |  |  |  |  |
|  | Precision DC Clamp meter Make Fluke- 325 / 319 | no |  | 12 |  |
|  | - Digital Multimeter- 1500 V DC make Fluke | no |  | 6 |  |
|  | - Portable Drill – upto 10 mm make Bocsh / Stanley | no |  | 2 |  |
|  | - Air blower – 820 W portable Bosch / Stanley | no |  | 12 |  |
|  | - Vacuum Cleaner, 1100 W Industrial Eureka Forbes | no |  | 6 |  |
|  | - Electrical Tool Kit Stanley / Taparia | no |  | 12 |  |
|  | - Mechanical Tool Kit Stanley / Taparia | no |  | 12 |  |
|  | - Portable hand Grinder 4” make Bosch / Stanley | no |  | 6 |  |
|  | - All Special tools recommended by Equipment manufacturers | Lot |  | 1 |  |

NOTE:

- Spares requirement for any equipment/system not specified above, the Bidder shall supply the spares for the supplied system / sub-System / instruments as per the manufacturer’s recommendation.

- The Bidder shall provide absolute numbers of spares based on percentage of installed items as agreed above after final design approval.

- (1)The suggested spares are the minimum requirement of GIPCL. The Bidder shall ensure sufficient spares beyond the suggested spares list to maintain its contractual
obligations.
(2) Bidder shall furnished recommended spare list as a part of design/drawing approval stage.
(3) Wherever % indicated in Mandatory spares list, Total installed quantity of each type shall be considered for calculation of % of spare of each type.
(4) For rounding of upper side number shall be considered for quantity of item.
(5) All the mandatory spares may be kept at site with record of use by Contractor during
O&M. Used items shall be replenished by Contractor time to time. All mandatory spares
items shall be handed over to GIPCL after completion of O&M period.

# SCHEDULE-VI PROCEDURE FOR PERFORMANCE GUARANTEE (PG) TESTING

## PART A: OPERATIONAL ACCEPTANCE TEST (OAT) PROCEDURE

Performance Ratio (PR) - Test Procedure

- Performance Ratio as determined through the PR test procedure specified here should not be less than 75% for Operational Acceptance Test (OAT).

- The Performance Ratio test to prove the guaranteed performance parameters of the power plant shall be conducted at site by the Contractor in presence of the Owner. The Contractor's Engineer shall make the plant ready to conduct such tests. The Operational Acceptance Test shall be commenced, within a period of one (1) month after successful Commissioning and, there will be continuous monitoring of the performance for 30 days. Any extension of time beyond the above one (1) month shall be mutually agreed upon. These tests shall be binding on both the parties to the Contract to determine compliance of the equipment with the guaranteed performance parameters. This monitoring will be performed on the site under the supervision of the Owner/ Owner's engineer.

- The test will consist of guaranteeing the correct operation of the plant over 30 days, by the way of the efficiency rate (performance ratio) based on the reading of the energy produced and delivered to the grid and the incident solar radiation (Average of all the pyranometers shall be considered for calculation of PR). During 30 Days period, the daily PR shall be calculated considering the cumulative irradiation, Energy exported and daily average PV module temperature as measured in the SCADA (During sunrise to sunset). The daily PR shall be again averaged for entire 30 Days and which shall be greater than or equal to 75%. In case non-availability of Grid (which is beyond the control of EPC contractor) the period of the same shall be excluded for calculation of the PR.  During the entire 30 days PR measurement period(s), minimum availability of the plant shall be 99%. If the PR greater than or equal to 75%, then the Operational Acceptance Test (OAT) shall be considered successful

- PR shall be demonstrated against the installed DC capacity.

- The efficiency or performance ratio (PR) of the PV plant is calculated as follows (according to IEC 61724).

- Performance Ratio (PR):

Where:

- Emeas,j = Produced energy (kWh) over each metering interval j;

- Pnom   = Nominal power of the PV plant (kWp). Sum of the individual module power

of all installed modules as per the relevant data sheets.

- Gj 	     = Irradiation (kWh/m²) measured per each metering interval j with an on-site

pyranometer with an identical inclination to the modules. Average

measurement of the installed pyranometers shall be considered.

- Gref       = 1 kW/m2  , irradiance at STC conditions.

- PRday  = Average PV plant PR during the testing period

- Tmeas,j  = Average module temperature (°C) measured during each metering interval j

by the temperature sensors placed on the back side of the modules.

Weighted average measurement of the installed module temperature sensors      shall be considered.

- β       = Weighted average of power temperature coefficients of the PV modules as

per the relevant data sheets. β shall be a negative value; and

- j 	    =  Interval for PR test (i.e., sunrise to sunset duration of a day).

- Monitoring System for PR Verification

The following instrumentation will be used to determine the Solar Plant Performance:

- ABT main meter at the delivery point at PSS 2 at 33 kV switchgears for point of measurement for energy yield (YA).

- Power meter for each inverter for reference only.

- Calibrated pyranometer to determine irradiance on the plane of array (with a target measurement uncertainty of ± 2%).

- Calibrated pyranometer to determine irradiance on horizontal plane (with a target measurement uncertainty of ± 2%).

- Thermocouples to measure module temperature with a measurement uncertainty of ±1°C.

- Shielded ventilated thermocouple with a measurement accuracy of ±1°C (for reference only).

- An anemometer mounted on a 10 m mast to measure wind speed (without additional shadowing on modules).

- Data measurement shall be witnessed in the format mutually agreed before the start of PR test by GIPCL and the Contractor jointly for the said period.

- The Contractor shall show the specified PR for Operational Acceptance.

## PART B:  ANNUAL TARGETED GENERATION TEST PROCEDURE

- Weather stations with calibrated pyranometers shall be installed by the Contractor at the location mutually agreed by the Contractor and GIPCL. The test report for the calibration shall be submitted by the Contractor for approval by GIPCL. The calibration should be traceable to a national / international laboratory. The output of this pyranometer for shall be logged in the SCADA system.

- In case the pyranometer is found to be working erratically then immediately the Contractor shall take necessary steps to rectify and / or recalibrate the instrument to the satisfaction of GIPCL. However, for the dispute period for which such error has occurred and until the instrument is recalibrated to the satisfaction of GIPCL, data from any one of the following lists of sources as decided by GIPCL will be used:

i. A separate pyranometer installed by the Owner near the site, if available

ii. Average of two closest solar power projects, as identified by GIPCL

iii. Nearest MNRE weather station

- “Actual Delivered Energy” from the plant supplied by the Contractor shall be noted (at ABT main meter installed in 33 kV switchgears at 400/33 kV Pooling Substation-2 at) for every month and summed up for entire year. For this purpose, the net delivered energy at the metering point shall be considered.

- The Contractor shall share with GIPCL all the irradiation, generation, etc. parameters details and all other factors necessary for GIPCL to corroborate the estimate. GIPCL has the right to cross verify data submitted by the Contractor by all possible means / sources.

Following factors may be noted for computing the PR and Targeted Generation Test:

- Effect due to variation in annual insolation shall only be considered for computing the PR/Targeted Generation.

- Effect due to variation of meteorological parameters e.g., ambient temperature, module temperature (except PR calculation), wind speed, humidity etc. shall not be considered.

- Generation loss due to grid outage (or power evacuation restriction by GIPCL / Grid authority which is beyond the control of Contractor or any other factors beyond the control of contractor for justified reasons accepted by GIPCL): The measured global solar radiation of the period of the outage of the power evacuation system shall be excluded to calculate average global solar radiation for the period of PR and Annual Targeted Generation test.

- In case, the GHI is not available because of instrumentation or SCADA problem, the corresponding insolation and generation shall be excluded from the time block for estimation of loss of generation and test shall be extended for the same outage period.

- Based on the parameters for PVSyst given in the tender (including solar irradiance, various loses etc.) and final .PAN file of PV module given by the GIPCL the first year Targeted Generation shall be derived by the contractor and the same shall be binding to the Contractor.

- PVSyst Version (Version V7.3 or latest), which shall be considered during detail engineering, the same Version shall be considered for arriving / calculating the targeted generation for the three (3) year O&M Period.

- The degradation for the second and third year of generation shall be 0.7% annually.

- In case the actual irradiation for particular year on annual basis is higher than given in the tender the Targeted Generation (Corrected Targeted Generation) shall also increase proportionately (subject to capacity for evacuation of power beyond 33 kV switchgear at pooling substation 2).

- In case the actual irradiation for particular year on annual basis is lower than given in the tender then the Targeted Generation (Corrected Targeted Generation) shall be reduced proportionately.

- In case Bidder is not able to achieve the corrected targeted generation then the penalty @ Rs. 2.73/kWh shall be applicable (Plus GST).

- In case bidder has generated higher generation then Targeted Generation then incentive shall be applicable (@ Rs. 0.20/kWh which is including GST).

- The illustration is given as follows:

The reference global horizontal irradiation (GHI) considered for Target Generation is as per follows:

TABLE 1: REFERENCE GHI DATA AT PROJECT SITE

| MONTH | GHI (kWh/m2) | Albedo |
| --- | --- | --- |
| JANUARY | 134.4 | 0.27 |
| FEBRUARY | 157.5 | 0.27 |
| MARCH | 213.5 | 0.27 |
| APRIL | 205.9 | 0.27 |
| MAY | 227.7 | 0.27 |
| JUNE | 179.8 | 0.27 |
| JULY | 169.8 | 0.27 |
| AUGUST | 145.1 | 0.27 |
| SEPTEMBER | 180.2 | 0.27 |
| OCTOBER | 184.5 | 0.27 |
| NOVEMBER | 147.7 | 0.27 |
| DECEMBER | 126.5 | 0.27 |
| TOTAL | 2072.6 | 0.27 |

All other parameters except irradiance to be considered for PVSyst simulation are as follows:

Bidder is free to propose his design of the solar plant including solar plant layout, solar block sizing, inverter sizing, inverter-transformer sizing etc. subject to meeting the boundary conditions / design parameters as specified in the table below. Bidder would be required to submit design details for 540 Wp Modules as well as actual Wp that would be supplied by Owner, during detailed engineering. However, for the purpose of bidding consideration, only the design for 540 Wp is to be considered.

- GIPCL is planning to install 8 Nos of Wind Turbine Generator (WTGs) on periphery of the plot (as per the following tentative locations). Bidder shall leave the shadow free area while preparation of Overall array layout. The Hub Diameter of WTG shall be considered as 150 Meters and hub height shall be 150 M. The exact Locations of WTGs shall be decided during detail Engineering.

Bidder shall consider above WTG’s shadow to meet Targeted generation.

Figure -1

TABLE 2: VARIOUS PARAMETERS TO BE CONSIDERED FOR PVSYST SIMULATION

| Sl. No. | Parameters | Value |
| --- | --- | --- |
|  | AC Capacity of the Plant | 500 MW |
|  | DC Capacity of the Plant | 625 MWp |
|  | Solar PV module (bifacial) rating* | 545 Wp |
|  | Solar PV module characteristic* | 2274 mm x1134 mm 34 kg (weight) 13.73 A (Isc) 28 modules in series The Pig tail cable length(s) shall be 300 to 500 mm. Bidder shall consider daisy chain stringing arrangement only. |
|  | Additional parameters of PV modules | Bifaciality factor: 70% Rear shading factor: 5% Rear mismatch factor: 10% |
|  | IAM losses | As per PV module .PAN file |
|  | Albedo | As per the Table -1 above |
|  | Inverter characteristic | As per Bidder’s consideration (Bidder shall provide .OND file) |
|  | Minimum pitch* | 5.2 m (for 1P arrangement) |
|  | Tracker | 1P single axis E-W tracker |
|  | Thermal loss factor (Uc, Uv) | Uc-29 W/m2-K Uv-0.0 W/m2-K m/s |
|  | Module quality loss | +0.1% |
|  | Module mismatch loss | 1.0% |
|  | String mismatch loss | 0.1% |
|  | Soiling loss | 1.0% |
|  | LID Loss | 2.0% |
|  | DC cabling loss at STC + AC cabling loss at STC | 2.5% (DC and AC cabling loss shall be as per system design chosen by Bidder) |
|  | IDT loss (for 33 kV transformer) | As per transformer datasheet, 1.1% max. |
|  | Auxiliary energy loss | 6 W/kW |
|  | Unavailability |  |
| a. | Unavailability time fraction | 1.0% |
| b. | Number of periods | 3 |
| c. | Unavailability time period | 16 January, 7 May & 21 July |
|  | Grid power limitation | 500 MW AC |

* Based on the actual module size and / or rating, the parameters may be modified suitably as per site conditions. However, for purpose of post award engineering and design, Bidders shall assume all above parameters with due design margins (say, 1% to 3% variation) to arrive at critical resultant design values and shall design the overall system accordingly so that the overall project progress is not affected adversely.

The example for calculation of annual Targeted Generation is as follows.

Example: In case Targeted Generation after providing actual .PAN file and data sheet of PV module is 1333 GWh for 500 MW (AC) / 625 MWp solar project.

Based on above, the Targeted Generation for Three years during O&M period is as follows.

| Sr. No. | Year | Target Generation | Yearly Degradation |
| --- | --- | --- | --- |
| 1 | First year of O&M | 1336 GWh | - |
| 2 | Second year of O&M | 1329 GWh | 0.6% |
| 3 | Third year of O&M | 1321 GWh | 0.6% |

Illustration - 1: In case actual annual cumulative GHI is 2100 kWh/m2

Corrected Target Generation for first year = (1336 X 2100) / 2072 = 1354 GWh/annum

Case-1: If actual Generation is higher than Corrected Generation then applicable incentive (@Rs.0.20/kWh) is payable by GIPCL to the Contractor.

As example if Actual Generation is 1370 GWh then incentive shall be payable to the bidder for additional generation

Additional Generation= (1370-1336) = 34 GWh

Incentive Payable to the Contractor by GIPCL

= 34x10,00,000 x0.20

= Rs. 6800000/- (including GST)

Case-2: If actual generation is lower than Corrected Generation than applicable penalty @Rs.2.73/kWh plus GST shall be payable by Contractor to the GIPCL / GIPCL shall recover the penalty from running bill or available bank guarantees.

If Actual Generation is 1300 GWh then penalty shall be payable by the bidder to GIPCL

Loss of Generation = (1336-1300) =36 GWh

Penalty to be paid to GIPCL by the Contractor

=36 x 10,00,000 x 2.73

= Rs. 98280000 /- (Plus GST)

Illustration – 2: In case actual annual cumulative GHI is 2000 kWh/m2

Corrected Target Generation for first year = (1336 X 2000) / 2072 = 1289 GWh/annum

Incentive and penalty shall be applicable as given in above illustration – 1.

# LIST OF ANNEXURES

## ANNEXURE – 1:	ELECTRICAL KEY SLD

## ANNEXURE – 2:	PRELIMINARY SCADA ARCHITECTURE

## ANNEXURE – 3:	SITE INVESTIGATION REPORT

## ANNEXURE – 4:	OVERALL PLANT LAYOUT (500MW) WITH PERIPHERAL FENCING

## ANNEXURE – 5:	TYPICAL PVC COATED CHAIN LINK PERIPHERAL FENCE DETAILS

## ANNEXURE – 6:	TYPICAL CABLE TRAY PRECAST SUPPORT

## ANNEXURE – 7:	TENTATIVE OVERALL SINGLE LINE DIAGRAM OF 400/33KV GIS PSS-2 SUBSTATION

## ANNEXURE –8:	GA DRAWING OF 33KV PEB NUMBER 3 & 4 OF PSS-2

## ANNEXURE –9:	TENTATIVE SPECIFICATIONS, DETAILS, DRAWINGS AND SCOPE OF 33KV SYSTEM OF PSS-2 (FOR ADDITIONAL FEEDERS OPTED BY BIDDER FOR ONLY SPACE UTILIZATION)

## ANNEXURE 9A - 	TENTATIVE GTP OF MAIN BREAKER PANEL AND ASSOCIATED DEDICATED METERING PANEL

## ANNEXURE 9B - 	TENTATIVE GTP OF ABT METER

## ANNEXURE 9C - 	TENTATIVE SCHEMATIC OF MAIN BREAKER PANEL

## ANNEXURE 9D - 	TENTATIVE SCHEMATIC OF ASSOCIATED DEDICATED METERING PANEL

## ANNEXURE 9E - 	TENTATIVE GA DRAWING OF MAIN BREAKER PANEL

## ANNEXURE 9F - 	TENTATIVE GA DRAWING ASSOCIATED DEDICATED METERING PANEL

## ANNEXURE 10 - 	TENTATIVE LAYOUT OF 400-33 KV PSS-2

## ANNEXURE 11 - 	SIMPLIFIED CONCEPTUAL COMMUNICATION ARCHITECTURE 500MW