VOLUME – II

PART – 2

SCOPE OF WORK & TECHNICAL SPECIFICATIONS

# TABLE OF CONTENTS

| Section | Description | PAGE NO. |
| --- | --- | --- |
|  | SCHEDULE-III |  |
|  | EPC Technical Specification | 3 |
| B | AC SYSTEM |  |
| B.1 | Inverter Duty Transformers | 3 |
| B.2 | 33 kV HT / MV Switchgear | 27 |
| B.3 | Auxiliary Transformers | 46 |
| B.4 | LT Auxiliary Switchboards | 57 |
| B.5 | UPS and UPS Distribution board | 67 |
| B.6 | 110V Battery and Battery Charger | 76 |
| B.7 | LT Power & control cables | 92 |
| B.8 | 33kV Power Cables | 103 |
| B.9 | SCADA system | 115 |
| B.10 | Fibre Optic Cables | 163 |
| B.11 | SEM (ABT) Tariff Metering System | 176 |

# SCHDULE – III EPC TECHNICAL SPECIFICATION

# AC SYSTEM

## B1 – INVERTER DUTY TRANSFORMER

|  | Inverter Duty Transformer |
| --- | --- |
|  | The design, manufacture, delivery, factory testing and inspection, delivery to site, installation, testing and commissioning of Continuous Solar Inverter application and Inverter duty (Outdoor) Transformers as per latest applicable standards. The equipment shall be designed, engineered and manufactured to achieve high availability and reliability. The supplier shall arrange all specialized equipment / services necessary for proper erection, commissioning, and performance testing of all items of the equipment covered under this contract. The cost of the same shall be included in the contract price. All routine and acceptance tests at Factory and Site acceptance tests shall be conducted as part of the contract with prior notice to Owner. |
|  | Codes & Standards |

|  | Codes | Description |
| --- | --- | --- |
|  | IS:2026 | Specification for Power Transformers |
|  | IEC:60076 | Power Transformers |
|  | IEC 61378-1 | Converter duty Transformers |
|  | IS 3639 | Fittings and Accessories for Power Transformers |
|  | IS 2099 | Specification of HV Porcelain Bushing |
|  | IS 7421 | Specification of LV Porcelain Bushing |
|  | IS 10028 | Practice for selection, installation & maintenance of transformers |
|  | IS 335 | New Insulating oils |
|  | CBIP | Manual on Transformers |
|  | IEC:60296 | Fluids for electro technical applications – Unused mineral insulating oils for transformers and switchgear |
|  | IEC:60354 | Loading guide for oil-immersed power transformers |
|  | IS 3637 | Buchholz Relay |
|  | IS 5561 | Specification for terminal connector |
|  | IS 6600 | Specification for overloading of Transformers |
|  | IS 2147 | Marshalling Box |
|  | IEC-60137 | Transformer bushings |
|  | IS-2705 | Specification for Current Transformers |
|  | IEC-61869 | Bushing CT |
|  | IS 4257 | Porcelain Bushings for Transformers |
|  | IS 10561/IS 8478 | Application Guide for on load tap changer & Power Transformers |
|  | IS 1893 | Criteria for earthquake resistant design of structures. |
|  | IS 5 | Painting |
|  | Indian Electricity Act and rules framed there-under |  |
|  | Regulations laid by the office of the Chief Electrical Inspector to Government. |  |
|  | BEE Guidelines |  |
|  | CEA Regulation on Technical Standards for Construction of Electrical Plants and Electric Lines, 2022. |  |
|  | Latest additions of (as applicable as on date of bid submission) NFPA, HEI, ANSI, ASME, ISI, TEMA, AWS, NEMA, IEC, EJMA, codes and standards shall also apply, Unless covered otherwise by Indian codes & standards and in case nothing to the contrary is specifically mentioned elsewhere in the specifications |  |

|  | Design Criteria - Inverter step up transformer shall be able to step up the inverter output voltage to 33kV. The voltage ratio and kVA rating shall be decided by the Bidder based on the system offered. - The transformers shall be of Converter Duty, two / multi winding, three phases, 50Hz, mineral oil filled, ONAN cooled, with off-circuit taps of ±5% in steps of 2.5% on the HV side. - Transformers should be provided with separate galvanically isolated low voltage windings for each inverter. - Transformers shall be suitable for operation with pulsed inverters. - Inverter Transformers with winding material of electrolytic grade copper / electrolytic grade Aluminum shall be acceptable subjected to proven and of successfully type tested design with service warrantee of 5 years after commissioning. - The thermal design of Inverter Transformer needs to consider the temperature dependent performance of the Inverter. It is to in accordance with Inverter output and under worst condition it should not limit Inverter output. - The design ambient temperature for the transformer shall be 50⁰C. - The transformer shall be designed for exceptional circumstances arising due to sudden fluctuation in power and supply voltage and shall be capable of operating at approximately 25% above normal rated voltage for a period of not exceeding one minute and 40% above normal rated voltage for a period of 5 seconds - The transformer shall be designed to deliver rated MVA continuously even at the lowest tap without exceeding specified temperature rise. The transformer and accessories shall be designed taking into account site conditions and other relevant project data indicated in Project Information. - All Transformers should be rated for a maximum temperature rise of 50°C by oil temperature and 55°C by winding temperature with a daily average ambient temperature of 50°C. Hot spot temperature based on maximum yearly weighted average temperature shall not exceed as per IEC standard recommendation - Transformers and accessories shall be designed to withstand the expected fault levels. Dynamic ability and thermal ability to withstand the short circuit forces shall be demonstrated by tests / calculations. - Transformer Differential protection shall be provided for Rating 10MVA and above. - The percentage impedance of transformer shall be as per Inverter manufacturer recommendation. - The transformer shall be capable of continuous operation at rated MVA on any tap with voltage variation of ±10% corresponding to the voltage of the tap as well as in accordance with IEC 60354 or other relevant standard. The transformer shall be capable of operating at rated output at any tap position, provided the voltage corresponding to that tap does not vary by more than ±10% of rated voltage. The winding including the tapping arrangement shall be designed such that the electromagnetic balance is maintained between HV and LV windings at all voltage ratios. - The transformer shall be provided with windings (all) and oil temperature indicators and double float type Buchholz relay (conforming to IS:3637) with gas collecting device & pipe and potential free contacts for remote alarm and trip purpose. The transformer shall be provided with minimum two numbers of spring-operated PRD (with trip contacts) with suitable discharge arrangement for oil. - For multi winding transformer, it is recommended to have close coupling and equal impedances on each of LV winding to HV winding and to have high enough impedance between two LV windings in order to decouple these windings. The multi-winding transformer needs to be designed for long term operating conditions with asymmetrical load on LV side i.e., in case three winding design, the transformer needs to operate reliable with only one Inverter supplying power to only one LV winding. - All tank gaskets used shall be of NBR (Acrylonitrile butadiene Rubber generally known as NBR) and properties of all the above gaskets / O-Rings shall comply with the requirements of IS-11149 (Grade IV) and manufacturer shall provide 5 years leakage free Warranty. - 2mm Thick CRCA sheet steel, vermin and dust proof marshalling box (minimum IP55) shall be furnished with each transformer to accommodate winding and oil temperature indicators, Buchholz relay, MOG, PRD contacts, Transducers and other contacts terminal blocks for control cables etc. Marshalling Box of all transformers shall be preferably Tank Mounted. One dummy terminal block in between each trip wire terminal shall be provided. At least 20% spare terminals shall be provided on each panel. The gasket used shall be of neoprene rubber. Also Marshalling Box, shall be at least 450 mm above ground level. Wiring scheme (TB details) shall be engraved in a stainless-steel plate with viewable font size and the same shall be fixed inside the Marshalling Box door - Transformer Neutral Earthing shall be done as per system requirement. In case of solidly earthed neutral of Transformers, it shall be brought through insulated support from tank to the ground level at a convenient point with 2 nos. copper flat, for connection to ground network (as applicable). The transformer neutrals shall be brought out in a separate cable box. If the same cable box is used for neutral side, then a metallic partition between phases and neutral shall be provided.. - Neutral of Transformer if not used should be taken out through bushing and covered by insulating cap. - The tank shall be of conventional / bell type with bolted cover on top. In case the joint is welded it shall be provided with flanges suitable for repeated welding. The joint shall be provided with a suitable gasket to prevent weld splatter inside the tank. Proper tank shielding shall be done to prevent excessive temperature rise of the joint. - The Inverter duty transformer shall be suitable for cable connection on HV and LV sides. In case of single core cable termination, cable box gland plate shall be of non-magnetic material. - The inverter transformer shall be provided with shield earthing. - The transformer shall be capable of being loaded in accordance with IEC 60354 / IEC 60076-7 upto a load of 150%. There shall be no limitation imposed by bushings or any other associated equipment. - Bushing CTs - Bushing CTs of adequate rating for protection (differential and others if any) as required, WTI etc shall be provided. All CTs (except WTI) shall be mounted in the turret of bushings, mounting inside the tank is not permitted. - For 33kV side PS Class CT for Transformer differential protection shall be provided in HV Turret of Transformer. - All CT terminals shall be provided as fixed type terminals on the M. Box to avoid any hazard due to loose connection leading to CT opening. In no circumstances Plug In type connectors shall be used for CT. Each IDT shall have additional Instrument Transformers, If required for Disturbance Recorders. Instrument Transformers Secondary wirings shall be routed to the separate box (In close proximity to LV cable boxes) for each winding of IDT. For CT circuit disconnecting type TB shall be provided with minimum two nos of spare TBs. PT circuit shall have 4 nos of single pole MCBs. If it is required to tap Auxiliary supply from IDT, then Current limiting MCCBs shall be provided in separate box near to the LV cable box. Any wiring inside the cable boxes shall be routed through high temperature rated conduits only - The transformers shall be suitable for outdoor installation in a hot, saline, humid and tropical climate. They shall be capable of operating continuously at their rated outputs without exceeding specified temperature limits. - Harmonic Factor as per Inverter manufacturer recommendation must be taken into account while designing the transformer. The extra no load loss due to voltage harmonics and load and stray load loss due to current harmonics (as applicable) and must be taken into consideration in transformer design. In addition, the dc bias component of 0.5% of rated Inverter output current is to be accounted for its effect on the transformer design. - The maximum flux density in any part of the core and yoke at the rated MVA, voltage and frequency shall be 1.76 Tesla and under 110 % continuous overvoltage condition it shall be 1.9 Tesla at all tap positions. - The line terminals of the windings of a three-phase power transformer shall be denoted by reference letter 1U, 1V, 1W for HV side and 2u, 2v, 2w, 3u, 3v, 3w and so on for LV sides. The neutral terminal shall be denoted as 1N for high voltage and 2n, 3n and so on for low voltage winding. If several windings have the same rated voltage, their respective numbering shall be agreed between the manufacturer and the purchaser. The numbering shall commence at the tapping nearest to the end marked 1. The marking of tapped windings which may be reversed shall be based on that connection which gives the highest effective number of turns for the winding connected to the tap-changer. - The noise level of transformer, when energized at normal voltage and frequency shall not exceed, when measured under standard conditions, the values specified in NEMA standard publication TR-1. - Transformer shall be suitable for oil filling by full vacuum. - The adverse effect on life of transformer due to cloud intermittency and solar generation loading cycle must be compensated through suitable design (as applicable). - Bushing turrets, covers of inspection openings, thermometer pockets etc. shall be designed to prevent ingress of water into or leakage of oil from the tank. - All bolted connections shall be fitted with weather proof, hot oil resistant, resilient gasket in between for complete oil tightness and shall give satisfactory service under the operating conditions for complete life of the transformer if not opened for maintenance at site. If gasket is compressible, metallic stops/other suitable means shall be provided to prevent over-compression. - All seams and joints which are not required to be opened at site, shall be factory welded, and shall be double welded [i.e. with a continuous cord on both sides of the plate (inside and outside of the tank), bottom & cover of the tank, turrets, flanges, etc.] to ensure adequate strength. Butt welds on parts that are mechanically stressed or under pressure must have full penetration. Welding shall conform to IS 9595. The requirement of post weld heat treatment of tank/stress relieving shall be based on recommendation of IS 10801. - Drain valves, shut off valves, oil sampling valves and filter valves shall be provided. A ladder with hand rail shall be provided to approach Buchholz relay, PRD, etc. Ladder shall start from 100mm above gravel level to Top of the transformer tank. The ladder shall have pad lockable cover right from start to avoid unauthorized climbing in transformer charged condition and with top hand rail. - The core shall be constructed from high permeability grade, non-ageing, cold rolled, grain oriented, silicon steel laminations. CRGO Silicon steel shall be M4 grade or better. The construction core shall comply to IS 3024. Core material shall be BIS certified. - The manufacturer shall ensure that windings of all transformers are made in clean, dust proof (Cleanroom class ISO 9 or better as per ISO 14644-1), humidity-controlled environment with positive atmospheric pressure. - Conductors shall be of electrolytic grade Copper / electrolytic grade Aluminum (of proven and of successfully type tested design with service warrantee of 5 years after commissioning) free from scales and burrs. Oxygen content shall be as per IS 12444. - Inverter Transformer shall have copper/Aluminum Shield winding between LV & HV windings. Each LV winding must be capable of handling non-sinusoidal voltage with voltage gradient as per relevant applicable standards and Inverter manufacturer recommendation. Also, each shield winding shall be taken out to tank with two separate connection from shield to bushing with proper support with 2 nos. 3.6 kV shield bushings and same shall be brought down along with support insulator from tank & copper flat up to the bottom of the tank for independent grounding. - Main conservator shall have air cell type constant oil pressure system to prevent oxidation and contamination of oil due to contact with moisture and shall be fitted with magnetic oil level gauge with low oil level potential free contacts at one side and prismatic oil level gauge at other side. Air cell used shall be made of nitrile rubber reinforced with nylon cloth suitable for operating continuously at 100°C. Pressure gauge shall be provided for Air cell to monitor air cell pressure. - The MOG and prismatic oil level gauge should not be obstructed with radiator bank, and it should be clearly visible from ground. Material for viewing window / glass for all items shall be Toughened glass only. - The conservator shall be fitted with lifting lugs in such a position so that it can be removed for cleaning purposes. Suitable provision shall be kept to replace air cell and cleaning of the conservator as applicable. - Suitable oil topping arrangement shall be provided at conservator top. - Suitable air venting arrangement shall be provided at over Tank, conservator tank, radiators, etc. - The Transformer tank conservator shall be fitted with cobalt free Silica gel Breather (in transparent enclosure with maximum height 1400mm above ground). Silica gel shall be isolated from atmosphere by an oil seal - Suitable extended SS304 canopy / Rain hood shall be provided for Buchholz relay, PRD/PRV, MK, MOG, JBs, Panel, cubicles, TCIV, NIFPS Fire detectors, etc. to prevent ingress of rain water. - Transformers shall be provided with a 150 mm dial type thermometer for top oil temperature indication with angular sweep of 270°. Range of temperature should be 0-150°C. - Temperature indicator dials shall have linear gradations to clearly read at least every 2°C. Accuracy class of OTI shall be 1.5% or better. OTI shall be with mercury free switches, (Ref: Precimeasure Type: 1005A or, equivalent of approved vendor). - 150 mm dia with angular sweep of 270° local winding temp. indicating instrument with maximum reading pointer and two adjustable electrically independent, ungrounded contacts (one for high winding temperature alarm and one for trip) besides that required for SCADA monitoring system shall be provided for HV and each LV windings. Temperature indicator dials shall have linear gradations to clearly read at least every 2°C. Range of temperature should be 0- 150°C. Accuracy class of WTIs shall be 1.5% or better. WTIs shall be with mercury free switches preferably of Type: 1005A or, better; Make: Precimeasure or equivalent of approved make. - The WTIs shall also be provided with in built variable resistor for connecting it to transducers for remote monitoring of the temperature. The transducers shall be provided with dual outputs of 4-20mA signal and shall be mounted in the cooler control cubicle / marshaling box. This is applicable to all windings. - Transducer Temperature Sensors for OTIs & WTIs: Temperature transducer with PT100 sensor RTD shall be provided with PT100 temperature sensor having nominal resistance of 100 ohms at 0°C. The PT100 temperature sensor shall have three wire ungrounded system. The calibration shall be as per IS 2848 or equivalent. The PT100 sensor may be placed in the pocket containing temperature sensing element. RTD shall include image coil for OTI system and shall provide dual output 4-20mA for SCADA. The transducer shall be installed in the Individual Marshalling Box. Any special cable required for shielding purpose, for connection between PT100 temperature sensor and transducer, shall be in the scope of manufacturer. 4-20mA signal shall be wired to SCADA through IEC 61850 compliant communications. - The transformers shall be provided with flanged bi-directional wheels and axles. This set of wheels and axles shall be suitable for fixing to the under carriage of transformer to facilitate its movement on rail track. Suitable locking arrangement along with foundation bolts shall be provided for the wheels to prevent accidental movement of transformer. - To prevent transformer movement during earthquake, suitable clamping devices shall be provided for fixing the transformer to the foundation. All Wheels shall be detachable and shall be made of cast iron and steel as required. - Suitable rating HV Bushings porcelain type with creepage – 31 mm/kV and LV Bushing below 3.6 kV used within transformer cable box, epoxy type bushing with creepage – 31 mm/kV confirming to IS 2099/IEC 60137 also allowed as alternate to porcelain type. Creepage distance shall be 31 mm/kV for all type of Bushings. - Inverter Transformer HV & LV bushings palms shall be silver/tin plated - The Step-up transformer shall be suitable for cable connection on HV side and LV sides. Suitable cable terminating arrangements shall be provided. In case of single core cable termination, cable box gland plate shall be of non-magnetic material - Air insulated dry Cable box for HT/LT XLPE cable shall be provided on HV & each LV Sides. Cable Box (Bolted design) with Disconnecting Chamber and cover with Handle shall be provided for cables terminations for HV & LV sides. Cable boxes shall be of phase segregated air insulated type & shall be of sufficient size to accommodate cable & termination and allow proper heat dissipation due to high current. Adequate measures to be applied to take-care of heat dissipation. Phase segregation shall be achieved by insulating barriers. Each LV winding of IDT shall be provided with separate cable box. - For each terminal shall be brought out through bushings with suitable rated Copper Bus bars / terminal connectors of sufficient size, copper flexible jumpers, supporting insulators, and bolt holes to accommodate cable & termination and allow proper heat dissipation due to high current. - Cable boxes shall be of 3mm sheet for load bearing member and 2mm for other parts with degree of protection as IP:55 or better as per IS:13974 - Proper two-point earthing and minimum two nos. GI supports shall be provided to each cable boxes. For effective cable earthing of LV side of IDTs, Earth Tag with serrated washer shall be provided in each cable gland. Each earth tag to be earth with 2.5 sqmm copper flexible wire to the gland plate of LV box. - Cable boxes shall have removable top cover with handle & ample clearance shall be provided to enable either transformer or each cable to be subjected separately to high voltage test. - The creepage distances of 31mm/kV and clearances for phase to earth and between phases shall not be less than those specified in standards. - Where cable boxes are provided for three core cables, the seating sockets on the two outer phases shall preferably be inclined towards the center to minimize bending of the cable cores. Where there is more than one core per phase, the socket block shall be so designed as to minimize bending of the cable cores. - Suitable size detachable type Gland plate of non-magnetic material shall be provided. The clear spacing of 900mm shall be provided between gland plate to terminals. All Gland plates shall be provided with drain plug. - Cable boxes shall be designed such that it shall be possible to move away the transformer without disturbing the cable terminations, leaving the cable box on external supports (as applicable). - Cable boxes shall be suitable for withstanding minimum fault current 31.5 kA for 1 Sec & 50 kA for 1 Sec for HV & LV respectively. - All joints shall be provided with weatherproof gasket and earthing link. - All joints shall be provided with canopy (inverted U-shape). Drain plug shall be provided. - The insulating oil shall be new, unused mineral oil, conforming to IEC-60296-2020/ IEC 61099 / IS 16081 / IS335. NO inhibitors shall be used in the transformer oil & conform to parameters specified at Annexure– E attached of Standard Technical Specifications of Transformer(s), while tested at Bidder's premises. The transformer shall and all associated oil filled equipment shall normally be supplied along with the first filling of oil and excess quantity of oil as per standard mentioned above. The Bidder shall furnish test certificates from the Bidder against their acceptance norms, prior to dispatch of oil from refinery to site. - The final coat shall be of a glossy oil and weather resisting non-fading paint of shade number RAL 7035 of IS:5. The paint shall be suitable for heavily polluted atmosphere. Primer paint shall be ready made zinc chrome as per IS: 104; intermediate and final coats of paint shall be as per IS: 2932. Color shade of final coat shall be RAL 7035. Sufficient quantity of touch-up paint shall be furnished for application at site. - The painting of all structures & equipment shall be considering C5-M corrosion zone as per "ISO-12944" for very high saline zone. Painting process shall be approved by the Owner. Color shade of final coat shall be RAL 7035 for external and White for internal. - The Bidder shall arrange transportation of all equipment from the point of manufacture to the Site. The arrangements shall include, but not be limited to, hiring adequate capacity of Wagon, determination of routes, determination of required permits, payment of required taxes and duties, and notification to the Owner. If transformer transported without oil, then shall be transported with filling Nitrogen gas / dry air at a positive pressure. - Radiators shall be detachable type, mounted on the tank with shut off valve at each point of connection to the tank, lifting lugs, along with drain plug/valve at the bottom and air release plug at the top. - All plates (rating plates, name plates, Valve schedule plate, Oil filling and Aircell instruction plate, instruction plates, etc.) and all labels shall be SS 304 with engraved letters. Minimum thickness of the plate shall be 1mm. All plates shall be fitted in a visible position, showing the appropriate items indicated below - All power and control cable glands shall be weather proof Double compression type made of heavy duty brass machine finished and nickel chrome plated of suitable size. Thickness of nickel plating shall not be less than 10 micron. Cable glands shall conform to BS:6121. - All Cable lugs for power cables shall be Heavy duty Long barrel tinned copper ring type / bimetallic solderless crimping type of suitable size. Cable lugs for control cables shall be tinned copper ring type with insulated sleeve. - All control terminal shall be of Stud type (screw drive operated) and control wiring shall be terminated with tinned copper ring type lugs with insulated sleeve. Disconnecting stud type terminal shall be provided for CT circuits. 20% spare terminal shall be provided of each type. Printed single tube ferrules marked to correspond with panel wiring diagram shall be fitted at both ends of each wire. The wire identification marking shall be in accordance with IS:375. Red Ferrules should be provided on trip circuit wiring. Fill factor shall be 40%. - All wiring shall be carried out with wires of 1.1 KV grade, stranded copper conductors. The insulation shall be halogen free and flame retardant. Power circuits shall be wired with stranded copper conductors of adequate sizes to suit the rated current, the minimum size shall be 2.5 sq. mm. Unless otherwise specified, control alarm and indication circuits shall be wired with stranded, tinned copper conductors of sizes not smaller than 1.5 sq. mm. Space heater circuits, CT and VT circuits shall be wired with stranded copper conductor of size not smaller than 2.5 sq. mm. - All metallic hardware such as nuts, bolts, screws, washers etc. shall be of SS-304. - All cable entries shall be located at bottom side of the panels / Junction boxes / MKs /DBs etc to prevent any possibility of water ingress into the box. All panels/Junction boxes/MKs /DBs etc shall be min. 450mm above finished floor level for cable connections. - Outdoor panels / JBs / MKs /DBs / Buchholz relay / PRD / MOGs / all cubicle etc shall be completely weather-proof with a sloping extended SS304 canopy for protection against rain and providing a degree of protection of IP 55. - Internal Paint shed shall be white. - Unless noted otherwise, all steel structures exposed to environment would be painted to meet the requirements of corrosion category or would be galvanized as specified in Project Information section. - Design shall be as per Seismic Zone - V of IS 1893 |  |
| --- | --- | --- |
|  | Transformer Fire Protection System |  |
|  | Transformer Fire protection system to be provided by bidder as per CEA Central Electricity Authority Regulations, CBIP manual of transformer standard /TAC/IS10028/IS 1646 and applicable regulations/guidelines/circulars/norms etc amended from time to time. |  |
|  | The supply of Nitrogen Injection Fire Protection system (NIFPS) system shall be included in scope of IDT Vendor. Warranty of NIFPS shall be part of IDT package. The specifications are as under - NIFPS system shall be selected and supplied by Transformer Manufacturer as an integral part of Transformer package, not to be supplied under different package by EPC contractor/bidder. - The offered make and model of NIPFS shall be reputed make and Transformer Manufacturer had supplied the same NIFPS in in their majority supply of the transformers in last five years . Transformer Manufacturer shall submit documentary evidence in support of supplied NIFPS system in last five year. - The bidder shall be responsible for the design of the complete system and shall submit the drawings and design calculations for the number of fire detectors, pipe sizing of drainpipe and Nitrogen injection pipe, Nitrogen cylinder capacity, number of injection points, etc. and get approval from Owner. - Facility shall be provided to test the system when the transformer is in service, without actually draining the oil and injecting Nitrogen. - The Nitrogen regulator valve shall be designed in such a way that the Nitrogen shall not enter the transformer tank even in case of passing/ leakage of valve Each Inverter duty transformer shall be provided with a dedicated Nitrogen Injection system. It shall act as a fast and effective fire fighter without employing water or carbon dioxide. Fire shall be extinguished within 3 minutes of system activation and within 30 seconds of commencement of nitrogen injection. Nitrogen Injection system shall consist of the following components. - Fire Extinguishing Cubicle placed on a plinth at a distance of about 5 m away from transformer. NIFPS shall be suitable for outdoor installation. Only Cubical mounting foundation may be required. considering ease of approach for manual operation in case of fire. The cubicle should house a pressurized nitrogen cylinder, connected to the oil tank of transformer. The Transformer Conservator Isolation Valve (TCIV) shall be fitted between the conservator tank and Buchholz relay. The Cubicle shall be made of CRCA sheet of 2 mm (minimum) thick complete with the base frame, painted inside and outside with post office red colour (shade 538 of IS -5. The degree of protection shall be IP55 or better. The following items shall be provided in the Cubicle. - Nitrogen gas cylinder with regulator and falling pressure electrical contact manometer. - Oil drain assembly including Oil drainpipe with mechanical quick drain valve. - Electromechanical control equipment for draining of oil of pre-determined volume and injecting regulated volume of nitrogen gas. - Pressure monitoring switch for back-up protection for nitrogen release. - Limit switches for monitoring of the system. - Butterfly valve with flanges on the top of panel for connecting oil drain pipe and nitrogen injection pipes for transformer. - Oil drain pipe extension of suitable sizes for connecting pipes to oil pit. - Panel lighting and Space heater. - Pressure indicators for Nitrogen pressure of the cylinder and actual injection through Nitrogen regulator. - Fire Extinguishing Cubicle shall have oil leakage detection arrangement for detecting oil leakage from drain valve. In case of any oil leakages, alarm to be provided. - Specifications for oil tank shall be as per below: - Minimum Oil Tank cover Size: 750X 750 mm - Material: Cast Iron - Type: Heavy duty Air tight - Painting inside and outside of the tank - Capacity of the tank as per CEA regulations and or Statutory requirement. - Air venting mechanism - Method to avoid rain Water or drain water entering the tank - A pit / sump of appropriate size in a corner of the tank shall be provided by Bidder with adequate slope to facilitate suction of the pump for complete emptying of the tank. Suitable pump with motor with automatic operation and its supply feeder shall be provided. - A Control box shall be placed in the inverter station for monitoring system operation, automatic control and remote operation. Separate control box for each transformer is to be provided. Enclosure of control box shall be of Rittal or equivalent. Two or more transformer control box in one enclose shall not be acceptable. Potential Free contacts shall be available for alarm troubles for input to . A separate hooter & emergency trip provision shall be provided in inverter station. Control box shall also to be connected to relay panel in inverter station for receiving system activation signals. Control supply voltage shall be of 110V DC. The following alarms, indications, switches, push buttons, audio signal etc. shall be provided. Only DIN mounted auxiliary contactors (of approved vendor) with or without add-on block are to be provided for signaling / contact multiplication etc. Use of miniature relays / plug-in relays are not acceptable. - System ON. - TCIV open. - TCIV closed - Oil drain valve closed. - Gas inlet valve closed. - Detector trip. - Buchholz relay trip. - Oil drain valve open. - Extinction in progress. - Cylinder pressure low. - Differential relay trip. - PRD / RPRR trip. - Transformer trip. - System out of service. - Fault in cable connecting fault detector. - Fault in cable connecting differential relay. - Fault in cable connecting Buchholz relay - Fault in cable connecting transformer reactor trip. - Fault in cable connecting PRD. - Fault in cable connecting TCIV. - Auto / Manual / Off - Extinction release on / off - Lamp test. - Visual / Audio alarm for AC supply fail. - Visual / Audio alarm for DC supply fail. - Alternatively, redundant supply can be provided - One feeder from UPS - One feeder from ACDB - If DC power is required for NIFPS the power converter shall be included in the NIFPS system. Power supply monitoring shall be provided in any supply fail it shall be recorded and alarmed in SCADA. - NIFPS shall be able to tolerate +/- 10 to 15 % voltage fluctuation. - Transformer conservator isolation valve (TCIV) shall be fitted in the conservator pipeline, between conservator and Buchholz relay which shall operate for isolating the conservator during abnormal flow of oil due to rupture / explosion of tank or bursting of bushing. The valve shall be flow sensitive and shut off when the flow in the pipe is more than the flow expected in the permissible normal operating conditions. The valve shall not isolate conservator during normal flow of oil during filtration or filling or refilling, locking plates to be provided with handle for pad locking. It shall have proximity switch for remote alarm, indication with visual position indicator. The TCIV should be of the best quality as malfunctioning of TCIV could lead to serious consequence. The closing of TCIV means stoppage of breathing of transformer. A suitable platform and ladder shall be provided to approach Buchholz relay and the TCIV valve for manual reset. Ladder shall start from 100mm above gravel level. The ladder shall be pad lockable cover right from start to avoid unauthorized climbing in transformer charged condition and with top handrail. - The system shall be complete with adequate number of detectors (quartz bulb) fitted on the top cover of the transformer oil tank. Detectors shall be connected in parallel to the signal box by Fire survival cables. Fire survival cables (capable to withstand 750 deg C.) shall conform to BS 7629-1, BS 8434-1, BS 7629-1 and BS 5839-1, BS EN 50267-2-1 or relevant Indian standards. - Signal box shall be mounted away from transformer main tank, preferably near the transformer marshalling box, for terminating cable connections from TCIV & detectors and for further connection to be control box. The degree of protection shall be IP55. - Fire Retardant Low Smoke Minimum FRLS or As per CEA regulation cable shall be used for connection between control box to DC & AC supply source, FEC to AC supply source, signal box / marshalling box to transformer conservator isolation valve connection on transformer. Separate cables for AC supply & DC supply shall be used. - Pipes complete with connections, flanges, bends and tees etc. shall be supplied along with the system. - Oil drain and nitrogen injection openings with gate valves on transformer tank at suitable locations. - Flanges between Buchholz relay and conservator tank for fixing TCIV. - Pipe connections between transformer and FEC and between FEC and oil pit required for collecting top oil. - Butterfly valves / Gate valves on oil drainpipe and nitrogen injection pipe which should be able to withstand full vacuum. - On receipt of all activating signals, the system shall drain - pre-determined volume of hot oil from the top of tank (i.e., top oil layer), through outlet valve, to reduce tank pressure by removing top oil and simultaneously injecting nitrogen gas at high pressure for stirring the oil at pre-fixed rate and thus bringing the temperature of top oil layer down. Transformer conservator isolation valve blocks the flow of oil from conservator tank in case of tank rupture / explosion or bushing bursting. Nitrogen occupies the space created by oil drained out and acts as an insulating layer over oil in the tank and thus preventing aggravation of fire. - Besides automatic control, remote electrical push button control at Control box and local manual control in the cubicle shall also be provided. Tripping of all circuit breakers (on HV & LV side) associated transformer is the pre-requisite for activation of system. - The following electrical signals shall be used for activating the system under prevention mode/fire extinguishing mode. For prevention: - Differential relay operation. - Buchholz relay paralleled with pressure relief Rise Relay For extinguishing: - Fire Detector (Type tested and calibrated) - Buchholz relay paralleled with pressure relief Relay. - The system shall be designed to be operated manually in case of failure of power supply to the system. It shall be ensured that once the system gets activated manually or in auto mode, all the connected breakers shall not close until the system is actually put in OFF mode. Also, PRD shall get closed only if all the connected breakers are open. - The supplier shall demonstrate the entire functional test associated with the following as Factory Acceptance Tests: - FEC, Control Box - Fire Detector - Transformer Conservator Isolation Valve - The performance test of the complete system shall be carried out after erection of the system with transformer at site. |  |
|  |  | Technical Parameters |

|  | Sl. No. | Item Description | Unit | Technical requirement |
| --- | --- | --- | --- | --- |
|  |  | Rating | kVA | To be decided based on Inverter rating and at least match with the PQ capability of Inverter at minimum ambient temperature 50 degree centigrade |
|  |  | Voltage ratio | kV | 33 / ** |
|  |  | Current Ratings | A | To be provided by bidder |
|  |  | Type | - | Oil filled Type |
|  |  | Type of Cooling | - | ONAN |
|  |  | Cooling Oil type | - | Mineral oil |
|  |  | Frequency | Hz | 50±5% |
|  |  | No. of windings of each transformer | - | Two / Multiwinding |
|  |  | Impedance @ base MVA | - | As per Standard and fault current limitation on LV side / as per inverter manufacturer’s recommendation |
|  |  | Surge Impedance |  | To be provided by bidder |
|  |  | Zero sequence Impedance |  | To be provided by bidder |
|  |  | Zero sequence Reactance |  | To be provided by bidder |
|  |  | Zero sequence Resistance |  | To be provided by bidder |
|  |  | Maximum current density |  |  |
|  |  | - LV Winding | A/ mm2 | 3.0 – 3.5 |
|  |  | - HV Winding | A/ mm2 | 3.0 – 3.5 |
|  |  | Maximum flux density | Wb/m2 | 1.76 |
|  |  | Winding connection and vector group | - | As per Inverter manufacturer’s recommendation |
|  |  | System earthing - HV - LV | - - | As per Inverter manufacturer’s recommendation |
|  |  | Type of tap changer | - | Off load-OCTC on HV side |
|  |  | Tapping range and number of steps | % | ±5 % in steps of 2.5 % |
|  |  | Loading Capability |  | Continuous operation at rated MVA on any tap with voltage variation of +/-10%, also transformer shall be capable of being loaded in accordance with IS:6600/IEC60076-7. As min. requirement, Transformers shall be designed with 110% continuous thermal overloading capability. |
|  |  | Over fluxing capability | % | 110% continuous 125% for 1 minute 140% for 5 seconds |
|  |  | Core | - |  |
|  |  | - Material | - | CRGO silicon steel laminations of M4 or better grade |
|  |  | - Thickness of lamination | mm | 0.27 or better |
|  |  | Winding | - | LV – Electrolytic Copper / Aluminium HV - Electrolytic Copper / Aluminium |
|  |  | Tank |  |  |
|  |  | - Material | - | As per Standard |
|  |  | - Thickness of sides | mm | As per Standard |
|  |  | - Thickness of top and bottom | mm | As per Standard |
|  |  | - Thickness of cover | mm | As per Standard |
|  |  | - Radiator Thickness | mm | Minimum 1 mm |
|  |  | Impulse withstand voltage of HV/LV winding | kVpeak | HV-170 LV- 10 |
|  |  | Power frequency withstand voltage of winding HV/LV | kVrms | HV - 70 LV - 3 |
|  |  | System Fault level for 1 sec. - HV Side - LV Side | kA kA | 31.5 As per Short circuit study |
|  |  | Permissible Temperature rise over an ambient of 50 deg C (irrespective of tap) |  |  |
|  |  | - Top Oil | Deg. C | 50 Deg. C |
|  |  | - Each Individual Winding | Deg.C | 55 Deg. C |
|  |  | Short circuit withstand time |  |  |
|  |  | - Three phase dead short Circuit at terminal with Rated voltage maintained on the other side. | Secs. | 2 |
|  |  | - Single phase short circuit at terminal with rated Voltage maintained on other side | Secs. | 2 |
|  |  | Clearances in air - Between Phases - Between Phase & Earth | mm mm | HV – 350, LV-55 HV – 250 LV-55 |
|  |  | Creepage distance | mm / kV | 31 |
|  |  | Noise level | - | As per NEMA TR-1 |
|  |  | Guaranteed Losses | % | Maximum 1.1% |
|  |  | - No Load Loss | % | Bidder to specify |
|  |  | - Load Loss | % | Bidder to specify |
|  |  | Terminal Connection |  |  |
|  |  | - 33 kV side | - | Phase segregated Cable box disconnecting Type |
|  |  | - LV side | - | Cable box disconnecting Type for each LV winding |
|  |  | Painting | - | Shade RAL 7035 external, Shade White Internal, as per C5-M Specifications |
|  |  | Winding Temperature Indicator (Local and Remote – to be integrated with SCADA) | - | On HV and each LV Windings |
|  |  | Oil Temperature Indicator (Local and Remote – to be integrated with SCADA) | Yes / No | Yes |
|  |  | Marshalling Box | - | Yes, outdoor type |
|  |  | - Degree of protection | - | IP 55 |
|  |  | Any other Data required for system studies or regulatory compliances or required by the Owner during detail engineering shall be provided |  |  |

Note : “**” – Indicates the data shall be as per Inverter Model chosen

Annexure – E  (Specification of Transformer Oil)

| Sr No | Property | Permissible Value |
| --- | --- | --- |
| 1 | Kinematic Viscosity, mm2 /s | 12 at 40 C 1800.0 at (-)30 C |
| 2 | Flash Point, C | 140 C |
| 3 | Pour point, C (-)40 C | Pour point, C (-)40 C |
| 4 | Appearance | Appearance Clear, free from sediment and suspended matter |
| 5 | Density kg/dm3 at 20 C | 0.895 |
| 6 | Interfacial Tension N/m at 25 C | 0.04 |
| 7 | Neutralisation value, mgKOH/g | 0.01 |
| 8 | Corrosive sulphur | Non-Corrosive |
|  | Presence of oxidation Inhibitor according to IS 13631 / IEC 60666, % | Not Detectable (< 0.01 % ) |
|  | Metal Passivator additives, mg/kg | Not Detectable (< 5 mg/kg ) |
|  | Other Additives | Does not contain any additives |
| 9 | Water content mg/kg | 30 in bulk supply 40 in drum supply |
| 10 | Anti-oxidants additives | Not detectable |
| 11 | Oxidation Stability - Neutralization value, mgKOH/g - Sludge, % by mass | 1.2 0.8 |
| 12 | Breakdown voltage - As delivered, kV - After treatment, kV | 30 70 |
| 13 | Dissipation factor, at 90 C And 40 Hz to 60 Hz | 0.005 |
| 14 | PCA content | 1% |
|  | PCB content | Not Detectable ( < 2mg /kg) |
| 15 | Impulse withstand Level, kVp | 145 |
| 16 | Gassing tendency at 50 Hz after 120 min, mm3 /min | 5 |

- Tests:

- Following type tests shall be conducted on one completely assembled transformer of each rating and each Make as per IS: 2026/ IEC-60076/CBIP Manual:

- Temperature rise Test with dissolved gas analysis test before and after.

- Dielectric tests (As per IEC 60076)

- Vacuum and pressure tests on Transformer tank, conservator, cooler units, pipe and other fittings.

- Degree of protection for Cooler control cabinet / Marshaling box

- Measurement of acoustic noise level as per NEMA TR-1 (special test)

- Testing of PRV / PRD, Buchloyz, MOG,

- Jacking test on complete assemble transformer

- Following minimum routine tests shall be performed on the Inverter Transformers as per IEC:60076 / IS:2026:

- Measurement of winding resistance-at all tap position

- Insulation resistance test

- Measurement of voltage ratio and check for vector relationship-at all tap    position

- Measurement of no load current with 415 V, 50 Hz AC supply

- Measurement of Impedance Voltage & short Circuit Impedance

- Measurement of No-Load Losses & current at 90%, 100% & 110% of rated voltage

- Measurement of Load Losses

- Induced Over voltage Withstand test

- Magnetic Balance and magnetising current Test

- Separate Source Voltage withstand test

- Oil BDV test

- Insulation Resistance & Polarization Index

- Measurement of capacitance & tan delta

- SFRA test

- Oil leakage test

- Calculation of Efficiency & Regulation

- Functional and continuity checking for marshalling box and auxiliary relays

- Shield earth connectivity

- Calibration check for OTIs, WTIs,  all CCUs.

- Testing of all Instrument Transformers.

- Special Test

Short Circuit Test: In case short circuit test has not been conducted or the test report not meeting the specification requirement for the offered transformer manufacturer, Bidder /Sub-vendor shall establish” Ability to withstand the dynamic effects of short circuit” for the offered transformer as per latest IEC 60076-5. The ability to withstand the dynamic effects of short circuit can be established either by performing actual short circuit test or by method of calculation with reference to short circuit tested reference transformer as per IEC-60076- 5 Bidder shall choose any one the two options mentioned below

- Option-1: Performing actual short circuit test as Type Test. In order to meet project schedule, Bidder/Sub vendor shall take suitable steps quite in advance to ensure successful conduction of short circuit test.

- Option-2: By theoretical evaluation of the ability to withstand dynamic effect of short circuit based on Calculation and Design and Manufacture Consideration. In this regard the guidelines given in Annexure-A with applicable tables of the IEC 60076-5 is to be followed.

- Data to be furnished by vendor after award of contract

  - Drawing / Document for Approval:

- Detailed technical data sheet

- Efficiency at full load and 75% load at unity power factor

- General outline drawings showing plan, front elevation, and side elevation, with all fittings and accessories, earthing terminals, foundation/floor fixing details, jacking pads and weights of the following:

- Marshalling box

- Cable boxes & disconnecting links

- Terminals details

- Conservator with Aircell

- Radiators

- Bushings: Plan, elevation, terminal details, mounting details, make and type number, current and voltage rating, creepage distance, etc.

- Rating and diagram plates drawing

- Valve schedule

- Type test certificate validity as per CEA

- Fire protection system OGA, drawing and documents with O&M manuals

- All accessories drawings like, OTI, WTI, breather, Buchholz Relay, PRD, Conservator, Radiator bank, etc along with catalogue with O&M manuals

- QAP and MQAP as per CEA regulations /standard/guideline Any other drawings / documents required by Owner during detail engineering

  - Drawings / Documents for information:

- Quality assurance plan, FAT/SAT procedure

- Field Quality Plan

- Product warranty document

- Schedule of manufacturing and delivery

- Detailed erection, testing & commissioning manuals

- Detailed operation and maintenance manuals

- Overloading Curve with time duration

- Recommended spare parts list for 5 years

- Printed instructions to receive, store and handle at site

- Any other drawings / documents required by Owner during detail engineering

## B2 - 33 KV HT / MV SWITCHGEAR

|  | 33 kV Sub-Pooling Switchboard and 33kV ICOG Panel |  |
| --- | --- | --- |
|  | The purpose of these panels is to provide necessary protection to Inverter duty transformers at the block level, aggregation of power and onward transmission to the 33kV pooling switchgear. The design, manufacture, delivery, factory testing and inspection, delivery to site, installation, testing and commissioning of these panels shall comply with latest applicable standards. The equipment shall be designed, engineered, and manufactured to achieve high availability and reliability. |  |
|  | The supplier shall arrange all specialized equipment / services necessary for proper erection, commissioning, and performance testing of all items of the equipment covered under this contract. The cost of the same shall be included in the contract price. |  |
|  | All routine and acceptance tests at Factory and Site acceptance tests shall be conducted as part of the contract with prior notice to Purchaser. |  |
|  | Codes & Standards |  |
|  | Codes; Description. IEC 60298; A.C. metal-enclosed switchgear and control gear for rated voltages above 1 kV and up to and including 52 kV. IEC 62271-100/200; High-voltage switchgear and control-gear. IS: 9921; A.C. disconnectors (isolators) and Earthing switches for voltages above 1000 V. IS: 9431; Specification for indoor post insulators of organic material for system with nominal voltages greater than 1000 volts up to and including 300 kV. IS: 2705; Current Transformers. IS: 3156; Voltage Transformers. IEC 60529; Degree of protection provided by enclosures (IP Code). IS: 6005; Code of practice for phosphating of iron and steel. IEC: 61850; Communication Standard for Numerical relays. IEC: 61131-3; Automation Standard for Numerical relays. IS :513 (2008); Cold Rolled Low Carbon Steel Sheets and Strips. IS: 9046; AC contactors for voltages above 1000 volts and up to and including 11000 Volts.. |
|  | Design Criteria - The Switchgear shall be of single tier, fully compartmentalized, metal enclosed construction type. - The switchgear shall have an internal arc test classification corresponding to system fault current and as per ICE62271-200. - The service class continuity of switchgear shall be LSC2B-PM as per IS/IEC 622771-200. - The Switchgear assembly shall be dust, moisture, rodent and vermin proof, with the truck in any position Service, Test / Isolated or removed and with all doors and covers closed. All doors, removable covers and glass windows shall have gaskets all round with synthetic rubber or neoprene gaskets - Cooling of Switchgear Panel shall by natural air flow. - HT Switchgear shall have a - Minimum Ingress degree of protection IP:42 for indoor application - Minimum Ingress degree of protection IP:55 or better for Outdoor application - Outdoor switchgear shall be provided with extended shed, plinth and working platform - Shall be resistant to water & ultraviolet radiation. - 33kV ICOG Panel shall be consisted of one VCB as the isolation and protection device. Indoor ICOG panel with Containerized solution or PEB building or outdoor ICOG panel with proper extended shed, plinth and working platform shall also be acceptable. Separate ICOG panel is also not mandatory in case distance between IDT and 33kV sub pooling station is less than 50 meters subject to compliance of electrical inspector’s requirements, safety regulation and any other applicable rules, norms, act, regulations etc. However additional hard wired EPB (Emergency Push Button) to be provided at strategic location in invertor station to trip the HT Breaker. - Each 33kV switchboard shall consists of VCB for the Inverter transformer incomers and VCB for the 33kV transmission line to the 400/33-33kV PSS-2 33KV pooling switchgear. The number of incoming feeders shall be decided based on the block configuration adopted for the project. Space provision for future panel (one no) shall be provided with each 33 kV switchboard. 33kV Sub-pooling switchboard shall be provided with RCC cum PEB building. - For MV/HT ICOG panels, following minimum clear distances shall be provided Front - 2500MM, Rear - 1750MM Left - 1500 mm Right - 1500 mm For MV/HT Panel boards, following minimum clear distances shall be provided Front - 2500MM, Rear - 1750MM Left - 1500 mm Right - 1500 mm Aisle – 3000 mm (distance between HT / MV panels / boards facing each other) For Future MV/HT Panels, following minimum clear distances shall be provided Left / Right – 300 mm - The circuit breakers and VTs shall be mounted on withdrawable trucks which shall roll out horizontally from service position to isolated position. Withdrawable bus VT’s shall be preferably on front side of the panel board. For complete withdrawal from the panel, the truck shall rollout on the floor or shall roll out on telescopic rails. In case the later arrangement is offered, suitable trollies shall be provided for each ICOG / Sub pooling stations (for each type of breaker) by the Bidder for withdrawal and insertion of the truck from and into the panel. Testing of the breaker shall be possible in isolated position by keeping the control plug connected - The ICOG panels shall consist of VCB for the incomer from Inverter Duty transformer. - Enclosure shall be constructed with rolled steel / Aluzinc / Stainless Steel sections and sheets metal of at least 2.5 mm thick. Detachable Gland plates of minimum 3 mm thick, shall be made out of hot rolled or cold rolled, for single core cables, it shall be nonmagnetic material. - Total height of the switchgear panels shall not generally exceed 2700 mm. The height of switches, push buttons and other hand operated devices shall not exceed 1800 mm and shall not be less than 700 mm from bottom of the panel base. All relays, meters, indicating lamps, switches etc. shall be flush mounted on the respective cubicle front door. - The VT/ relay compartments shall have degree of protection not less than IP:52 in accordance with IS:13947. However, remaining compartments of 33kV Switchgear shall have a degree of protection of IP: 42 (minimum) for indoor application. No louvers/opening shall be provided on the top of the panel. All other louvers if provided, shall have very fine brass or GI mesh screen. Tight fitting gourmet/gaskets are to be provided at all openings in relay compartment. - All VCB shall be motorized type. - Circuit breaker shall be restrike free, stored energy operated and trip free type. Motor wound closing spring charging shall only be acceptable. An anti-pumping relay shall be provided for each breaker. Spring charging motor winding shall be provided with Class -E or better insulation. - The closing coil and spring charging motor shall operate satisfactorily at all values of control supply voltage between 85% to 110% rated DC voltage. The shunt trip coils shall operate satisfactorily under all operating conditions of the circuit breaker up to its rated short circuit breaking current at all values of control supply voltage between 70% to 110% of rated DC voltage. - Breakers Operation Class shall be E2, M2 & C2 and Rated Operating Duty shall be O - 0.3Sec- CO-3MIN-CO. - In case, control supply availability is must for movement of breaker from service to test to isolate and vice versa, than dedicated MCB (other than protection and other control MCB’s) shall be provided for locking magnet / solenoid / similar device used for such interlock. - Each DC circuits (e.g. DC main sources, closing circuit, tripping circuit, indication circuit, spring charging motor circuit, auxiliary supply to indicating instrument etc.) shall have dedicated MCBs of required rating. - All AC Auxiliaries / control circuits shall have dedicated MCBs of required rating. - VCB shall have mechanically latched separate lock out relay (ABB PSU14X or VAJC or equivalent), trip circuit supervision of lock out relay and VCB in open and close condition, DC supervision and AC supervision (this can be a part of annunciator also). 2 NO and 2 NC spare contacts wired up to the TB shall be provided. - Breaker auxiliary contacts shall be used directly. In case contact multiplication is inevitable (only if OEM is not supporting number of auxiliary contacts required) then mechanically latched electrically operated contact multiplication relays (e.g VAJC / PSU14X) shall be provided. 2NO + 2 NC spare breaker auxiliary contacts wire up to TB for future use shall be provided. - Only DIN mounted auxiliary contactors (of approved vendor) with or without add-on block are to be provided for signaling / contact multiplication etc. Use of miniature relays / plug in relay are not acceptable. - The switchgear shall be fully integrated with SCADA and with IEC 61850. All feeders shall be controlled from SCADA / respective control system and from the switchgear. All the protection and safety interlocks shall be hardwired in the Switchgear itself. Bidder shall consider adequate number of digital inputs and outputs for integration with SCADA. Number of DI and DO will finalized during detail engineering without any extra cost to the owner. DI and DO shall be from numerical relay only (Additional RIO is not acceptable). - Mimic diagram with description of function to represent the single line diagram, shall be made available on the panel. - Suitable explosion vents to ensure safety of operating personnel shall be provided. - The switchgear shall be provided with emergency push buttons for emergency operations. - The panels shall be provided with internal illumination (LED lamp) along with utility power socket (6+16 Amp). - All working parts of the mechanism shall be of corrosion resisting material. - The circuit breaker shall normally be controlled from SCADA and local operation shall also be provided. - All circuit breakers shall be provided with communicable numerical relays with IEC 61850 protocol. - All control terminals shall be of Stud type (screw drive operated) and control wiring shall be terminated with tinned copper ring type lugs. Disconnecting stud type terminal shall be provided for CT circuits. Printed single tube ferrules marked to correspond with panel wiring diagram shall be fitted at both ends of each wire. The wire identification marking shall be in accordance with IS:375. Red Ferrules should be provided on trip circuit wiring. 20% of terminals of each type and rating in each feeder shall be provided as spare subject to a minimum of 2 terminals of each type and rating. - 110V DC Supply shall be used for control and protection system of switchgear. In case UPS AC supply is considered for auxiliary control and protection supply for ICOG switchgear, then suitably rated AC/DC converter/power pack arrangement with 100% redundancies shall be used to meet the DC control supply requirement of switchgear panels. - The Cable glands shall be weatherproof Double compression type made of heavy-duty brass machine finished, and nickel chrome plated of suitable size. Thickness of plating shall not be less than 10 microns. Cable glands shall conform to BS:6121. - All Cable lugs for power cables shall be Heavy duty long barrel tinned copper ring type / bimetallic solderless crimping type of suitable size. Cable lugs for control cables shall be tinned copper ring type with insulated sleeve. - The basic control scheme shall be developed in the numerical relay using programmable (soft) logics. - Facilities shall be provided for mechanical tripping of the breaker and for manual charging of the stored energy mechanism for a complete duty cycle, in an emergency in closed door condition. - The segregation shall be designed to prevent arcs, smoke and/or vaporized metal from going directly or indirectly from one compartment to another so as to prevent the fault or its effects spreading to other compartments. - Compartmenting shall be such that maintenance can be carried out safely on one (1) circuit with other adjacent circuits still in service. - The switchgear construction shall be such that the operating personnel are not endangered by breaker operation and internal explosions, and the front of the panels shall be specially designed to withstand these. Pressure relief device shall be provided in each high voltage compartment of a panel, so that in case of a fault in a compartment, the gases produced are safely vented out, thereby minimizing the possibility of its spreading to other compartments and panels. The pressure relief device shall not however reduce the degree of protection of panels under normal working conditions. Gas duct from panel to be routed to outside of PEB. - The surge arrestors shall be provided for inverter transformer feeders to limit the switching over voltages and for other feeders including 33kV Transmission line feeders as per system study requirement. The surge arrestors shall be of metal oxide, gapped or gap less type generally in accordance with IEC 60099- 4 and suitable for indoor duty. These shall be mounted within the switchgear cubicle between line and earth, preferably in the cable compartment. Surge arrestor specifications and ratings shall be as per insulation coordination study. Insulation coordination study is in scope of Bidder. - Surge arrestor selected shall be suitable for un-earthed system and rating shall be in such a way that the value of steep fronted switching over voltage generated at the switchgear terminals shall be limited to the requirements of switchgear. - The Currents Transformers (CT) and Voltage Transformers (VT) shall be provided for protection and metering and shall be cast-resin encapsulated type with insulation class 'F' or better. - CTs shall be rated for switchgear fault level for 1 sec and conforming to accuracy class mentioned below: - - Class PS for differential relaying - Class 5P20 for other relaying - Class 0.2s for ABT metering system with ISF, burden and ratio (obtaining approvals is in the scope of bidder) as per regulatory requirements /concern competent authority requirements. - Class 0.2s for general Metering for 33kV Transmission lines with ISF<5 - Class 0.2s or better for general metering for ICOG panel with ISF<5 - Space Provision for Line differential protection relay in LV compartment (with flush blanking plate), along with space for PS class CT in HT compartment (with required busbars) shall be provided for all 33kV transmission lines to 400/33-33kV PSS-2 for Owner future use. - PS Class CT for Transformer differential protection (33kV side) shall be provided in HV Turret of Transformer. - Separate cores shall be provided for metering and protection applications. Core balance CT and associated relay combination shall be such as to ensure a pickup sensitivity of 10 A primary ground fault current for all the outgoing feeders. - For SEM (ABT) Tariff metering System kindly refer Clause no. 1.3 of VOL-II Part-1. - Multifunction Meters for general purpose of accuracy class 0.2s with separate 0.2s class CT and 0.2 class PT to be provided for the each outgoing 33kV transmission line feeder to 400/33-33kV PSS-2 switchgear. - The List of parameters for all MFM shall be as per Secure Elite 445 or Rishabh RISH 3430. All parameters of the MFMs shall be integrated to the SCADA system. - VTs for 33kV switchgear with suitable HRC fuses on primary and MCBs on secondary sides, under voltage relays, remote annunciation on supply failure shall be provided. Following 33kV VTs shall be provided: - Line VTs for each 33kV transmission line - Bus VTs for each 33kV sub-pooling switchgear - 33kV ICOG panel (sub-pooling switchgear side) if connected to SPS then only Line VT shall be provided - 33kV ICOG panels if directly connected to PSS-2 then VTs shall be Provided on both sides of the Breaker - Accuracy class of the voltage transformers shall be as specified below. - Class 3P for protection - Class 0.2 for ABT metering system with burden (obtaining approvals is in the scope of bidder) as per regulatory requirements /concern competent authority requirements. - Class 0.2 for general Metering for 33kv Transmission line - Class 0.2 or better for general metering for ICOG panel - Power from inverter stations / blocks may be pooled at sub pooling stations and or power from Inverter station / block to be directly pooled to 33/400kV PSS-2 in line with bay allocation at PSS-2 - Metering system of 3-phase, 4 wire, 3 elements, 0.2s Class (0.2s class MFM, 0.2 Class VT’s and 0.2s class CT’s) shall be provided at HV side of each Inverter Transformer at the ICOG panel. - Separate earthing trucks shall be provided for all ICOG and all sub-pooling switchgears breaker feeders for maintenance work. These trucks shall be suitable for earthing the switchgear busbars / cables as well as outgoing and incoming cables. The trucks shall have a interlock to prevent earthing of any live connection. - As an alternative to separate earthing trucks, the Bidder may also offer built-in earthing switches for the busbars / cables and outgoing & incoming connections for all breaker feeders at all sub-pooling switchgears and all ICOG panels. Earthing switches if opted shall be standard proven switchgear design. The inbuilt earthing switches shall be quick make type, independent of the action of the operator and shall be operable from the front of the switchgear panel. These switches shall have facility for padlocking in the earthed condition. - Suitable arrangement for power cable termination shall be provided as required. Cable entry shall be from the bottom. The bottom cable entry shall be fitted with removable gland plates of adequate size for fixing cable glands. A minimum clearance of about 600 mm shall be kept between the cable lug bottom ends and gland plates for stress cone formation for XLPE cables. Interphase clearance in the cable termination compartment shall be adequate to meet electrical and mechanical requirement besides facilitating easy connections and disconnection of cables. Dimensional drawing of cable connection compartment showing the location of lug, glands, CTs, gland plates etc. and the electrical clearances available shall be submitted for owner’s approval during detail engineering - All wiring shall be carried out with wires of 1.1 KV grade, stranded copper conductors. The insulation shall be halogen free and flame retardant. Power circuits shall be wired with stranded copper conductors of adequate sizes to suit the rated current, the minimum size shall be 2.5 sq. mm. Unless otherwise specified, control alarm and indication circuits shall be wired with stranded, tinned copper conductors of sizes not smaller than 1.5 sq. mm. Space heater, CT and VT circuits shall be wired with stranded copper conductor of size not smaller than 2.5 sq. mm. - Compartment internal wiring truff fill factor shall not be more than 50%. LV compartment of the panel shall be spacious for any future requirement. (Minimum 20% additional space must be available) - Panel earthing arrangements to be provided and earth conductor location shall not obstruct access to cable terminations. - Hinged doors shall be earthed through flexible earthing braid. - Nameplates and instruction plates shall be provided for all switchgears. - Electrical Insulating mat (as per IS: 15652) shall be provided for all the panels (in front as well as back of the panel) as per statutory requirement to ensure safe operation. - The meters shall be suitable for operation from the secondary of CTs and VTs. They shall be provided with a separate test block (screw type, large size, three phase four wire) for the testing of the meters without disturbing the CT and PT secondary connections. Meters shall be equipped with communications interface with MODBUS protocol. - All protection relays shall be numerical type. Relays shall be preferably in draw-out cases with built-in test facilities or plug in type with proper testing facilities. All protective relays shall be provided with test blocks (with CT, PT, Trip circuit, auxiliary supply, logical input, and output contact) for online testing (Secondary injection) without disturbing wiring. Adequate numbers of multi finger test plugs shall be provided - Numerical relays shall have the minimum following features - Type of relays shall be latest numerical high end version with highest display size and features available in proposed make and its product range - At least two group of settings - Min. no of LEDs - 10 (Minimum 2 LED’s for future use) - Front key pad for Parameter / Navigation. - In built lockout function with front key resetting. - EMC Compatible. - No adopter / Convertor is acceptable. - At least 10 disturbance recorder - At least 5 Fault recorder - Event recording at least 50 - Unlimited logic gates - In-built timers - Freely programmable DI / DO. (Min 2 DI/DO for future use wired up to TB) - In built CB control function with interlocking. - Goose messaging for inter tripping command and interlocking in addition to hardware interlocking. - Non -Volatile memory with battery backup or suitable arrangement - Time synchronization - Self-diagnosis / watchdog / relay failure – two output contacts shall be configured. - All hardware and licensed software required for communication of relays, parameterization, download / analysis of fault data from relays and interfacing the relays with the SCADA system shall be supplied by the Bidder in complete with set of cables, accessories, etc. - All 33kV switchgear breaker feeders including ICOGs shall be provided with dedicated BCU or BCPU. - Following minimum protections shall be provided as specified below and any other required protections, functions, features, functionality required as per applicable regulation / norms / prudent industrial practices / system requirement shall be considered by the bidder without any extra cost to the owner. - Minimum Protections required for Inverter duty Transformers: - Transformer differential protection (87T) to be provided for Transformer of capacity 10 MVA and above - IDMT & DMT overcurrent protection (50/51) - IDMT & DMT earth fault protection (50N/51N) - Under voltage protection (27) - Over Voltage Protection (59) - Auxiliary relays for WTI (all windings), OTI, PRV1, PRV2, MOG, NIFPS, Buchholz etc. - Under frequency (81U) and over frequency (81O) - Instantaneous earth fault protection through CBCT (50 G) - Minimum Protections required for Incoming feeders of sub pooling stations (from Solar generation end): - IDMT & DMT overcurrent protection (50/51) - IDMT & DMT earth fault protection (50N/51N) - Under voltage protection (27) - Over Voltage (59) - Under frequency (81U) and over frequency (81O) - Instantaneous earth fault protection through CBCT (50 G) - Minimum protection required for Outgoing 33kV Transmission lines - IDMT & DMT overcurrent protection (50/51) - IDMT & DMT earth fault protection (50N/51N) - Instantaneous earth fault protection through CBCT (50 G). - Under voltage protection (27) - Over Voltage (59) - Under frequency (81U) and over frequency (81O) - Minimum protection required for Aux. Transformers (for 33KV Voltage class) - IDMT & DMT overcurrent protection (50/51) - IDMT & DMT earth fault protection (50N/51N) - Instantaneous earth fault protection through CBCT (50 G). - Under voltage protection (27) - Over Voltage (59) Auxiliary relays for WTI (all windings), OTI, MOG, Buchholz etc. - Relay cases shall have adequate number of terminals for making potential free connections to the relay coils and contacts including spare contacts. - Cable trench of HT panel board shall be designed after considering adequate margin of cable bending radius. Cable entry in the trench shall be at least above 1 meter to HFL (High Flood Level) - Annunciator (with AC and DC supply supervision) with SCADA integration to be provided for each feeder. (4 Nos of Spare window wired up to TB is to be provided in each annunciator). - Indication lamps shall be of the panel mounting, LED type. The lamps shall have escutcheon plates marked with its function, wherever necessary. LED indicating lamp shall be cluster type. Lamps shall have translucent lamp-covers as warranted by the application - Seismic Zone-V compliance for switchgear. - Hooter system is to be provided for each 33KV sub pooling switchgear board and ICOG panel. - Inter-cubicle looping of control and cubicle space heating supplies for all the panels of switchgear shall be carried out by the Supplier. - Aluminium or copper earthing bus shall be provided at the bottom and shall extend throughout the length of each switchgear. It shall be bolted to the framework of each panel and each breaker earthing contact bar. - Each switchgear cubicle shall be equipped with thermostatically controlled SS304 grade / Aluminium alloy space heaters to prevent moisture condensation within the enclosure and shall be complete with MCB for power supply. Heaters and MCB shall be suitable for continuous operation on 230V, 1 phase, 50 Hz AC supply. - All metallic hardware such as nuts, bolts, screws, washers etc. shall be of Hot dip galvanized as per IS standard. - 230V, 1 phase, 50 Hz. AC plug point shall be provided in the interior of each cubicle with an on-off switch for connection of hand lamps. - Metering/wiring cubicle shall be provided with LED fitting for illumination. - The temperature of busbar and all other equipment, when carrying the rated current continuously shall be limited as per the stipulation of IEC 62271-1 2017, duly considering the specified ambient temperature. - Busbars and connection shall be fully insulated for working voltage with adequate phase/ground clearances. Insulating heat shrink sleeves (colour coated) for busbars and cast-resin shrouds / silicon rubber shrouds for joints shall be provided. Cross section of the main horizontal busbar shall be uniform throughout the switchgear and continuous in one transport unit. All buses and connection shall be supported and braced to withstand stresses due to maximum short circuit current and also to take care of any thermal expansion. Make of HT cable sleeves shall be Hong Shang or Raychem. - Name plate shall be of non-rusting metal or 3-ply limacoid with white engraved letterings, on black background or as per manufacturer’s proven standards. Inscriptions and lettering shall be subjected to Owner's approval - Red colour Zebra lines to be provided to distinguishing the 33kV Transmission lines to PSS-2 (exact colour shade, thickness and spacing of Zebra lines shall be finalized during detail engineering). - Painting shall be carried out by approved process. Painting procedure and thickness of paint shall be suitable for saline environment as per ISO 12944. Corrosivity grade C5-M zone shall be considered for outdoor equipment. Corrosivity grade C4 Grade shall be considered for indoor equipment. After preparation of the under surface the equipment shall be painted with epoxy-based paint by powder coating. Final external shade shall be RAL-7035 and Internal shade shall be White. - Bidder to provide disconnecting type terminal blocks for associated instrument transformers to facilitate connection of external PMUs. External PMUs are in GIPCL scope. |  |
|  | Technical Parameters |

| Sl. No. | Description | Unit | Technical Requirements |
| --- | --- | --- | --- |
|  | Type of switchgear | - | Metal Clad Switchgear, Extendable at both ends, Outdoor / Indoor |
|  | Application |  | Outdoor / Indoor |
|  | Rated Voltage | kV | 33 ± 10% |
|  | Frequency | Hz | 50 ±5 % |
|  | Max. System Voltage | kV | 36 |
|  | Design Ambient Temperature | ⁰C | 50 |
|  | Max. Temp. rise limited | ⁰C | 90 for non-silver-plated joints 105 for silver plated joints |
|  | Auxiliary Supply (AC) | V | 230 |
|  | Auxiliary Supply (DC) | V | 110 |
|  | Humidity | % | 95 |
|  | System earthing | - | As per system requirement |
|  | Insulation level |  |  |
|  | a) Power frequency withstand Capacity for 1 min. | kVrms | 70 |
|  | b) Impulse Withstand Voltage | kVpeak | 170 |
|  | Short Circuit Withstand capability | kA | As per Maximum fault level considering PSS-2 400 KV Bus as infinite Grid / Bus. |
|  | Bus bars |  |  |
|  | - Material of bus bar | - | Aluminum EC-91 / Electrolytic grade Copper |
|  | - Cont. Current Rating of Busbar | A | As per system design study calculation |
|  | - Support insulators | - | Required |
|  | - Dynamic withstands current rating (min) | kAp | 63 |
|  | - Temperature rise of over design ambient of 50C Bus bars - Silver plated joints |  | 40C 55C |
|  | Switchboard Construction |  |  |
|  | - Material of construction | - | Sheet metal 2.5 mm thick CRCA / Aluzinc / Stainless Steel (minimum) suitable for outdoor / indoor application as per suitability to site condition. |
|  | - Thickness of Sheet steel |  |  |
|  | - Enclosure/ Frame/ Doors -CRCA | mm | 2.5 |
|  | - Front Door | mm | 2.5 |
|  | - Partition | mm | 1.6 |
|  | - Gland Plate | mm | 3.0 / 4.0 |
|  | Degree of Protection | - | IP42 for Indoor and for Outdoor Minimum IP55 with extended canopy |
|  | Paint Shade | - | RAL-7035 for External and White for internal. C4-M specification for indoor and C5-M specification for Outdoor |
|  | Earthing Bus Bar | - | Required, Size to be selected based on fault current |
|  | Minimum safety clearances in air |  |  |
|  | - Between phases | mm | 320 |
|  | - Between phase & earth | mm | 270 |
|  | Accessories for the Panels |  |  |
|  | - Locking facility | - | Required |
|  | - Lamp with switch | - | Required |
|  | - Power socket | - | Required |
|  | - Breaker Operation Counter | - | Required |
|  | - Power pack for Auxiliary DC supply for breakers | - | Power pack for ICOG panel 100% redundant and Battery bank for SPS |
|  | - Anti-pumping Relay | - | Required |
|  | - AC and DC Fail Relay | - | Required |
|  | - Space heater | - | Required |
|  | - Indicating lamps | - | Required |
|  | - Nameplate | - | Required |
|  | - Danger Plate | - | Required |
|  | Circuit Breaker |  |  |
|  | - Type | - | VCB |
|  | - System | - | EDO, 3 Pole |
|  | - Rated Operating Duty | - | 0 – 0.3S – CO – 3min – CO |
|  | - Rated Current | A | As per design requirement |
|  | - Short Circuit Breaking Current | kA | As per Maximum fault level considering PSS-2 400 KV Bus as infinite Grid / Bus. |
|  | - Short Circuit Making Current | kAp | 2.5 times of system fault current |
|  | - Opening time | - | 3 cycles |
|  | - Closing time | - | 4 cycles |
|  | - Spring Charging Motor | - | Required |
|  | - Auxiliary contacts | - | As per system requirement |
|  | Current Transformer | - |  |
|  | - No. of Cores | - | system requirement |
|  | - ISF |  | <5 |
|  | - Accuracy Class | - | As per system requirement |
|  | - CT Ratio | - | As per requirement |
|  | - Burden | VA | As per system requirement |
|  | - Short time rating | kA | As per Maximum fault level considering PSS-2 400 KV Bus as infinite Grid / Bus |
|  | - Type | - | Cast Resin |
|  | Voltage Transformers | - |  |
|  | - No. of Cores | - | As per system requirement |
|  | - Accuracy Class | - | As per System requirement |
|  | - Ratio | - | 33000/√3:110/√3:110/√3 |
|  | - Burden | VA | As per system requirement |
|  | - Type |  | Cast Resin |
|  | Current Transformer for SEM meter | - |  |
|  | No. of Cores | - | 1 |
|  | ISF |  | <5 |
|  | Accuracy Class | - | 0.2s |
|  | CT Ratio | - | As per statutory requirement |
|  | Burden | VA | As per statutory requirement |
|  | Short time rating | kA | As per Maximum fault level considering PSS-2 400 KV Bus as infinite Grid / Bus |
|  | Type | - | Cast Resin |
|  | Voltage Transformers for SEM meter | - |  |
|  | - No. of Cores | - | 2 |
|  | - Accuracy Class | - | 0.2 for metering |
|  | - Ratio | - | 33000/√3:110/√3:110/√3 |
|  | - Burden | VA | As per statutory requirement |
|  | Type |  | Cast Resin |
|  | Space heater | W | Rating to be calculated as per design |
|  | Seismic Acceleration |  | 0.36g |

- Tests

- The switchgear shall have valid Type Test Reports for the tests carried out within last ten years on equipment of similar rating/design shall be submitted for review (including Internal arc test as per IEC 622771-200, service class continuity test, LSC2B-PM as per IS/IEC 622771-200).

- Dielectric tests including Lightning impulse withstand test, Power frequency withstand test, switching impulse test, partial discharge test, artificial pollution test, Power frequency withstand test on auxiliary and control circuits

- IP protection test

- Short time and peak withstand test

- Temperature rise test

- Radio interference voltage tests

- Measurement of resistance of the main circuit

- The supplier of these panel shall be the Original Equipment Manufacturer (OEM) or channel partners.

- For circuit breaker, the list of type tests shall include the following minimum tests as per IS 13118:

- Dielectric tests

- Radio interference voltage test

- Measurement of the resistance of the main circuit

- Temperature-rise tests

- Short time withstand current, and peak withstand current tests

- Verification of the Protection

- Tightness tests

- Electromagnetic compatibility tests

- Mechanical and environmental tests including Mechanical operation test

- Short-circuit current making and breaking tests

- Capacitive current switching tests

- Magnetizing and inductive/capacitive current switching tests

- Internal Arc Test as per IEC

- Type test of, CT, PT, Relay etc. shall be as per IS/IEC standard.

- The switchgear shall be tested as per relevant standards. However, the following minimum tests shall be carried out compulsorily under routine tests along with other tests.

  - IR and HV Test

  - Functional operation of VCB

  - Electrical interlock test

  - Secondary injection test for relay and meters

  - Communication with SCADA and compatibility check

  - Earthing continuity test

- Tariff metering system including Tariff meter, CT/PT specifications, drawing approval, testing etc., including fees per requirement of WRLDC / RLDC/ SLDC/ STU / concern competent authority is in the scope of Bidder. For detailed specifications and scope also refer section Tariff Metering system.

- Data to be furnished by vendor after award of contract

- Drawings / Documents for Approval:

- Switchgear cubicle: outline dimensions and GA, including plan, front elevation, rear elevation, side elevation and relevant cross-sectional views.

- Switchgear layout plan including floor opening and fixing arrangement

- Schematic control circuit diagram

- Single line diagram & Schematic wiring diagrams

- Metering and protection drawing

- Short circuit withstand calculation for busbar (Thermal & dynamic)

- Detail wiring diagram including terminal block numbers, ferrule numbers and cable connection.

- Relay and instrument panel GA

- Inter panel interconnection wiring diagram

- Busbar sizing calculation

- Relay setting and relay co-ordination,

- Design calculations,

- MQAP and QAP as per CEA regulations

- Relay, CT, PT, Meter, related all items details drawing, catalogue

- Erection & Commissioning procedure, O& M manual

- Foundation Plan & loading details

- Catalogues / drawings / leaflets for all items

- Comprehensive memory mapping of all IEDs

- Any other drawings / documents required by the Owner during detail engineering

- Drawings / Documents for Information:

- Type test reports

- Manufacturer’s catalogues

- Erection manuals

- Any other drawings / documents required by the Owner during detail engineering

## B3 – AUXILIARY TRANSFORMER

|  | Auxiliary Transformers |  |
| --- | --- | --- |
|  | The design, material, construction, manufacture, performance, inspection and testing of Auxiliary Transformers shall comply with all latest versions of standards, statutes, regulations and safety codes in the locality where the equipment is proposed to be installed. |  |
|  | Codes & Standards The design, manufacture and testing of auxiliary transformers shall be carried out as per the latest applicable standards including but not limited to the following: |  |
|  | Codes | Description |
|  | IS:2026 | Power & Distribution Transformer |
|  | IS:11171 / IEC 60076 | Dry Type Transformers |
|  | IS:12063 | Degree of Protection Provided by Enclosures |
|  | IEC:60905 | Loading Guide for dry type transformers |
|  | IEC60296 | Fluids for Electrotechnical applications – Mineral insulating oil for electrical equipment |
|  | IS:2099 | Specification for Bushings for Alternating voltages above 1000V |
|  | IS 3639 | Specification for Fittings and accessories for Power Transformers |
|  | IS 10028 | Code of practice for selection, installation, and maintenance of transformers |
|  | IS 1180 | Outdoor/Indoor Type Oil Immersed Distribution Transformers upto and including 2 500 kVA, 33 kV |
|  | IS 3347 | Dimension for porcelain transformer bushings |
|  | IS 4257 | Porcelain Bushings for Transformers |
|  | IS 6600 | Guide for Loading of Oil Immersed Transformers |
|  | IS-2705 | Specification for Current Transformers |
|  | IEC 60076 | Power Transformers (All parts) |
|  | Indian Electricity Act 2003 and Indian Electricity Rules, BEE notification, CEA regulations, guidelines, CBIP Manual on Transformers |  |

|  | Design Criteria - Auxiliary Transformers - 20% design margin shall be added to the final calculation. Also, if required, the rating shall be increased to keep the voltage drop during starting of the largest motor within 15%. - The transformer shall conform to the latest editions of national and international standards indicated above. Also, the transformer shall comply with the requirements indicated in Technical Parameters. - The core shall be constructed from high grade non-ageing cold rolled grain-oriented silicon steel laminations of high grade or better quality. The insulation of core to clamp plates shall be able to withstand a power frequency voltage of 2 kV (rms) for one (1) minute. - Transformers and accessories shall be designed to withstand the expected fault levels. - The dry type transformers shall be housed in a metal protective housing, having a degree of protection of IP-23. In case it is placed outdoor, IP for enclosure shall be minimum IP-55. Enclosure shall be of a tested quality sheet steel of minimum thickness 2mm & shall also accommodate cable terminations. The housing door shall be interlocked such that it should be possible to open the door only when transformer is off. The enclosure shall be provided with lifting lugs and other hardware for floor mounting. Suitable bidirectional skids with pre-drilled holes shall be provided integral with the enclosure or bidirectional rollers shall be provided with suitable locking arrangement. - Winding conductor shall be electrolytic grade as per standard. Windings shall be of class F insulation or better. All windings are to be uniformly insulated. - The auxiliary transformer shall be suitable for cable connection on both HV and LV sides. Suitable cable terminating arrangements shall be provided for both sides. In case of single core cable termination, cable box gland plate shall be of nonmagnetic material. - MCB / MCCB shall be provided at Primary as well as secondary sides of DRY type Auxiliary transformers. Also, current limiting MCB/ MCCB shall be provided at source (IDT or inverter) for dry type low voltage aux. transformers. However, HT panel with circuit breaker and all required protections and control system shall be provided for high voltage aux. transformers in line with standards, statutory requirement and tender specifications. - If required, Transformer shall be provided with suitable ventilation system to ensure the temperature rise limits under most severe condition while in service however all tests and performance shall correspond to air natural cooling. - All materials used shall be of best quality and of the class, most suitable for working-under the conditions specified and shall withstand the variations of temperature and atmospheric conditions, overloads, over-excitation, short-circuits as per specified standards, without distortion or deterioration or the setting up of undue stresses in any part, and also without affecting the strength and suitability of the various parts for the work which they have to perform. |  |
| --- | --- | --- |
|  |  | - Auxiliary transformer of XX/0.415kV, suitable KVA rating shall be provided for meeting the Inverter block auxiliary loads / sub pooling station loads. The rating of the auxiliary transformer shall be based on the expected auxiliary loads of the Bidder’s complete system. - This transformer shall derive auxiliary power from the inverter / Inverter Transformer LV cable box / LT Panel in case of string inverter for Inverter block/station and or from 33kV board for sub pooling station and deliver to the 415V Main switchgear. Design shall be in such a way that Aux. supply of Inverter block shall be available in case of failure of incoming source supply (Auxiliary transformer to be fed from two inverters with suitable changeover switch) if Aux. supply shall be derived from Inverters. If Aux. supply shall be derived from any LV of IDT then no changeover switch shall be required and Aux. supply shall be derived through suitable current limiting MCCBs (with enclosure) mounted at cable box of that LV winding of IDT. - The transformers shall conform to the latest editions of national and international standards indicated in above. Also, the transformer shall comply with the requirements indicated in Technical Parameters. - Fittings which are generally required for satisfactory operation of the transformers are deemed to be included, in the scope of supply of the Bidder. - The Cable glands shall be weatherproof Double compression type made of heavy duty brass machine finished and nickel chrome plated of suitable size. Thickness of plating shall not be less than 10 microns. Cable glands shall conform to BS:6121. - All Cable lugs for power cables shall be Heavy duty long barrel tinned copper ring type / bimetallic solderless crimping type of suitable size. Cable lugs for control cables shall be tinned copper ring type with insulated sleeve. - All control terminals shall be of Stud type (screw drive operated) and control wiring shall be terminated with tinned copper ring type lugs with insulated sleeve. Disconnecting stud type terminal shall be provided for CT circuits. 20% spare terminal shall be provided of each type. Printed single tube ferrules marked to correspond with panel wiring diagram shall be fitted at both ends of each wire. The wire identification marking shall be in accordance with IS:375. Red Ferrules should be provided on trip circuit wiring. - All wiring shall be carried out with wires of 1.1 KV grade, stranded copper conductors. The insulation shall be halogen free and flame retardant. Power circuits shall be wired with stranded copper conductors of adequate sizes to suit the rated current, the minimum size shall be 2.5 sq. mm. Unless otherwise specified, control alarm and indication circuits shall be wired with stranded, tinned copper conductors of sizes not smaller than 1.5 sq. mm. Space heater circuits, CT and VT circuits shall be wired with stranded copper conductor of size not smaller than 2.5 sq. mm. - All Auxiliary transformers neutral earthing shall be provided with dedicated earthing pits, earth flat etc. - All metallic hardware such as nuts, bolts, screws, washers etc. shall be of Hot dip galvanized as per IS standard. - Painting of all metallic enclosed electrical panels / JBs / MKs /DBs etc shall be of paint shade RAL -7035 and Shall be as per ISO 12944-5, corresponding to minimum C5-M category specifications for outdoor equipment and C4-M category specifications for indoor equipment. Unless noted otherwise, all steel structures exposed to environment would be painted to meet the requirements of corrosion category or would be galvanized to minimum 110microns - Design shall be as per Seismic Zone - V of IS 1893 - All bolted connections shall be fitted with weather proof, hot oil resistant, resilient gasket in between for complete oil tightness and shall give satisfactory service under the operating conditions for complete life of the transformer if not opened for maintenance at site. If gasket is compressible, metallic stops/other suitable means shall be provided to prevent over-compression. - The maximum flux density in any part of the core and yoke at the rated KVA, voltage and frequency shall be 1.76 Tesla and under 110 % continuous overvoltage condition it shall be 1.9 Tesla at all tap positions. - The core shall be constructed from high permeability grade, non-ageing, cold rolled, grain oriented, silicon steel laminations. CRGO Silicon steel shall be M4 grade or better. The construction core shall comply to IS 3024. Core material shall be BIS certified - Transformers shall be provided with a 150 mm dial type thermometer for top oil temperature indication with angular sweep of 270°. Range of temperature should be 0-150°C. - Temperature indicator dials shall have linear gradations to clearly read at least every 2°C. Accuracy class of OTI shall be 1.5% or better. OTI shall be with mercury free switches, (Ref: Precimeasure Type: 1005A or, equivalent of approved vendor). - 150 mm dia with angular sweep of 270° local winding temp. indicating instrument with maximum reading pointer and two adjustable electrically independent, ungrounded contacts (one for high winding temperature alarm and one for trip) besides that required for SCADA monitoring system shall be provided for HV and each LV windings. Temperature indicator dials shall have linear gradations to clearly read at least every 2°C. Range of temperature should be 0- 150°C. Accuracy class of WTIs shall be 1.5% or better. WTIs shall be with mercury free switches preferably of Type: 1005A or, better; Make: Precimeasure or equivalent of approved make. - Drain valves, shut off valves, oil sampling valves and filter valves shall be provided for oil filled transformers. - The MOG and prismatic oil level gauge shall be provided for conservator tank and should not be obstructed with radiator, and it should be clearly visible from ground for oil filled transformers. - All viewing windows / glass shall be Toughened glass only. - The Transformer conservator shall be fitted with cobalt free Silica gel Breather (in transparent enclosure with maximum height 1200mm above ground). Silica gel shall be isolated from atmosphere by an oil seal. - Suitable extended SS304 canopy / Rain hood shall be provided for Buchholz relay, PRD/PRV, MOG, MK, JBs, Panel, cubicles, etc. to prevent ingress of rain water. - Bushings with Creepage distance of 31 mm/kV shall be provided for each Transformers. - Air insulated dry Cable box for HT/LT XLPE cable shall be provided on HV & LV Sides. Cable Box (Bolted design) with Disconnecting Chamber and cover with Handle shall be provided for cables terminations for HV & LV sides. Cable boxes shall be of phase segregated air insulated type & shall be of sufficient size to accommodate cable & termination and allow proper heat dissipation. Adequate measures to be applied to take-care of heat dissipation. Phase segregation shall be achieved by insulating barriers. Further detailed Cable box specifications shall be in line with Inverter Duty Transformer specifications. - The insulating oil as specified in Inverter Duty Transformer section shall be provided. - Radiators shall be detachable type, mounted on the tank with shut off valve at each point of connection to the tank, lifting lugs, along with drain plug/valve at the bottom and air release plug at the top. |

- Technical Parameters

4.1 Dry Type Transformer

| Sl. No. | ## Description | Unit | Technical Requirements |  |
| --- | --- | --- | --- | --- |
|  | Application | - | PV Block / Inverter station Auxiliary Loads |  |
|  | Type | - | Indoor 2 winding, Dry Type Epoxy cast resin/resin encapsulated |  |
|  | Power Rating | kVA | ** TBD during DE |  |
|  | Quantity | Nos. | As per requirement in multiples of XX kVA rating |  |
|  | Voltage rating |  |  |  |
|  | - Primary | V | XXV, 3 ph, 3 wire (suitable for inverter output voltage) |  |
|  | - Secondary | V | 415V, 3 ph, 4 wire |  |
|  | Impedance | % | As per relevant Standard |  |
|  | Rated Frequency | Hz. | 50 |  |
|  | Vector Group | - | Shall be finalised during detail engineering as per Owners requirement without any financial implication to owner |  |
|  | Full load loss @ 75ºC | kW | As per relevant Standard |  |
|  | System Earthing | - | Primary side as per system requirement and Solid Earthing on LV side |  |
|  | System Fault level | kA | As per system requirement during detailed engineering |  |
|  | Tapping: |  |  |  |
|  | - Tap range | % | -5% to +5% |  |
|  | - Tapping step | % | 2.5% |  |
|  | Type of voltage variation (CFVV/VFVV/CBVV) | - | CFVV |  |
|  | Over fluxing capability | - | 110% continuous |  |
|  | Type of Cooling | - | Air natural |  |
|  | Winding insulation type | - | Uniform |  |
|  | Power frequency withstand voltage of winding - HV winding - LV winding | kV (rms) | * 3 |  |
|  | Insulation class | - | F or better |  |
|  | Temp. rise above 50 °C - In winding by resistance | C | 70 |  |
|  | Conductor material | - | Electrolytic Grade Copper |  |
|  | Paint shade | - | RAL 7035 for external and White for Internal. Indoor C4-M / outdoor C5-M specifications |  |
|  | Ref. Standards | - | IS:2026, IS:1180 & IS:11171 |  |
|  | Terminal arrangement | - | PRIMARY | SECONDARY |
|  |  |  | Required | Required |
|  | Mounting type |  | Floor mounted with bottom Cable entry |  |
|  | Min. clearance in air (a) Phase-Phase (b) Phase-Earth | mm mm |  |  |
|  |  |  | 25 20 | 25 20 |
|  | Creepage distance | mm/kV | 31 | 31 |

4.2 Oil filled Transformer

| Sl. No. | Description | Unit | Data |
| --- | --- | --- | --- |
|  | Service |  | Outdoor, sub pooling station Auxiliary Loads |
|  | Type |  | Oil Filled type, two winding |
|  | No. of Phase |  | Three |
|  | Rating | kVA | As per System requirement |
|  | No. of windings |  | Two |
|  | Conductor material |  | Electrolytic Grade Copper |
|  | Nominal system voltage (HV / LV) | kV | 33/0.415 , 50 Hz |
|  | Vector group |  | To be finalised during detail engineering as per Owners requirement without any financial implication to owner |
|  | Type of cooling |  | ONAN |
|  | Impulse withstand level |  |  |
| a) | HV side | kV | 170 |
|  | One minute Power frequency withstand voltage |  |  |
| a) | HV side | kV | 70 |
| b) | LV side | kV | 3 |
|  | Connections |  |  |
| a) | HV side |  | to be decided during detail engineering |
| b) | LV side |  | to be decided during detail engineering |
|  | Neutral Earthing |  |  |
| a) | HV side |  |  |
| b) | LV side |  | Solidly grounded |
|  | Terminal arrangement |  |  |
| a) | HV side |  | Cable Box |
| b) | LV side |  | Cable Box |
| a) | LV Neutral side |  | Ground conductor |
|  | Bushings |  |  |
| a) | Bushings Creepage distance |  | 31 mm /kV |
|  | Tap Changer |  |  |
| a) | Type |  | OCTC |
| b) | Tap provided on |  | HV side |
| c) | Range of taps | % | +5% to –5% in steps of 2.5% |
|  | Short circuit withstand duration | Sec | 2 |
|  | LV neutral bushing CT |  | As per requirement |
|  | Energy Efficiency Class |  | BEE Level 1(As per latest amendment) |
|  | Losses |  |  |
|  | Copper Loss |  | As per IS |
|  | Iron Loss |  | As per IS |
|  | Impedance |  | As required to limit fault level below 50kA |
|  | Ref. Standards | - | IS:2026, IS:1180 & IS:11171 |
|  | Paint | - | RAL 7035 for external and White for Internal. Indoor C4-M / outdoor C5-M specifications |
|  | Buchholz Relay with alarm and tripping contacts and integrating to SCADA |  | Required |
|  | PRV with tripping contacts and integrating to SCADA |  | Required |
|  | OTI with alarm and tripping contacts and integrating to SCADA |  | Required |
|  | WTI for each windings with alarm and tripping contacts and integrating to SCADA |  | Required |
|  | SS 304 grade Canopy for each devices, name plate, Valve schedule plate, rating plate, etc., |  | Required |
|  | Gasket material |  | NBR (Acrylonitrile butadiene Rubber) |
|  | Radiator thickness |  | 1mm (minimum) |  |
|  | MOG with alarm contacts and integrating to SCADA |  | Required |  |

* Data to be furnished by Bidder

|  | TESTS The routine tests shall be carried out as per applicable standards on all the transformers. The following tests shall be performed compulsory as part of routine tests along with other tests as per manufacturer recommendation and as per 2026 and or IEC-60076 and or CBIP Manual and or CEA regulations shall also be carried out: - Ratio, polarity, phase sequence and vector group. - Resistance of windings at all tap position - Magnetic balance test and measurement of magnetizing current - Insulation resistance. - Measurement of Load loss and impedance - Dimensional check. - Dielectric Tests. - Calculation of Efficiency & Regulation - Functional and continuity checking for marshalling box and auxiliary relays - Oil leakage test on completely assembled transformer along with radiators for oil filled transformers Following Type test reports shall be furnished along with the offer: - Temperature rise test for determining the maximum temperature rise after continuous full load run. - Dielectric tests (As per IEC 60076). - Vacuum and pressure tests on Transformer tank, conservator, cooler units, pipe and other fittings. - Degree of protection for Marshalling box - Testing of PRV / PRD,MOG, buchloyz, Noise-level measurement. - Any other tests required by Owner during detail engineering |
| --- | --- |
|  | Data to be furnished by vendor after award of contract Drawing / Document for Approval and information: - Detailed technical data sheet - General outline drawings showing plan, front elevation, and side elevation, with all fittings and accessories, earthing terminals, foundation/floor fixing details, and weights of the following: - Transformer - Marshalling box - Cable boxes & disconnecting links - Terminals details - Bushing details - Conservators - Radiators - Rating and diagram plates, valve schedule etc. drawing - Any other required documents |

## B4 – LT AUXILIARY SWITCHGEAR

|  | LT Switchboards |  |
| --- | --- | --- |
|  | The design, material, construction, manufacture, inspection, testing and performance of 415V LT switchboards shall comply with all currently applicable statutes, regulations and safety codes in the locality where the equipment will be installed. The equipment shall also conform to the latest applicable standards mentioned in Codes & Standards. |  |  |
|  | Codes & Standards |  |  |
|  | Codes | Description |  |
|  | UL 746C | UV Resistant |  |
|  | IS-2147/ IEC 60529 | Degree of protection provided by enclosures (IP Code) |  |
|  | IEC 61439 | Standard for low voltage switchgear and control gear assembly |  |
|  | IEC 60352 | Crimped connections – general requirement, test methods and practical guide |  |
|  | IEC 61326-1 | Electrical equipment for measurement |  |
|  | UL 508 | Standard for Industrial Control equipment |  |
|  | IEC 62208 | Empty enclosure for low Voltage switchgear and control gear assemblies |  |
|  | IEC 60269-6 | Low Voltage Power Fuses |  |
|  | IEC 62262 | Level of Protection against Mechanical Impact (IK Rating) |  |
|  | IEC 60974 | Low-voltage switchgear and control |  |

|  | Design Criteria and general requirements - Incomer feeders of 415V switchboard shall be provided with suitable MCCB along with CT & MFM of accuracy class 0.5s or better for measurement of plant auxiliary consumption. MFMs shall have suitable communication port for integration with SCADA system. All outgoing Feeders shall be Provided with suitable MCB/MCCB/MPCB only. - MCCBs for incomers & bus-coupler shall be provided with auxiliary contacts to provide ON, OFF, TRIP feedbacks to SCADA & shunt trip. MCCB/MPCB/MCB, contactor and overload relay shall meet type 2 co-ordination as per applicable standard. All outgoing feeder shall be provided with suitable rated MCCB/MPCB/MCB, contactor and overload relay only. - The 415V LT switchboard shall be provided with thermostatically controlled SS304 / Aluminium space heater, cubicle lamp and utility power socket. - The 415V LT switchboard shall be suitable for floor mounting complete with gland plates, glands, body earthing terminals etc. single/double front and compartmentalised design. 415V LT switchboard shall be sheet steel enclosed and shall be dust, weather and vermin proof providing with degree of ingress protection IP: 42 as per IS/IEC 60947 for indoor application and IP:55 or better for outdoor application. All cut-outs shall be provided with EPDM / Neoprene gaskets. However, the control / relay compartments if provided shall have degree of protection not less than IP 5X. - The LT switchboards at sub pooling stations shall be equipped with two incomers (2X100%), and Bus coupler with auto change over facility (MCCB with Contactor/ MPCB/MCB plus Contactor), auto manual selection, required interlocks etc., Detail scheme shall be finalized during detail engineering as per Owner’s requirement. - All switchboard frames and load bearing members shall be fabricated using suitable mild steel structural sections or pressed and shaped cold-rolled sheet steel of thickness 2.0mm. Frames shall be enclosed in cold-rolled sheet steel of thickness 1.6 mm. Doors and covers shall also be of cold rolled sheet steel of thickness 1.6 mm. Stiffeners shall be provided wherever necessary. The gland plate thickness shall be 2.0 mm for hot / cold rolled sheet steel and 3.0 mm for non-magnetic material. Minimum clear distances (in mm) shall be as per below mention table for all LT switchboards, PDBs, DBs, Panels etc. Single Front; Double Front. Front; 1000; 1000. Rear; 400; 1000. Right; 400; 400. Left; 400; 400. - All sheet steel work shall be degreased, pickled, phosphated and then applied with two coats of zinc chromate primer and two coats of finishing synthetic epoxy paint, both inside and outside the paint shall be of colour shade RAL 7035 for external and white for internal and C5-M painting specifications for outdoor and C4-M painting specifications for indoor applications. - Two earthing terminals with SS304 grade nut, bolt, spring and plan washers of suitable size shall be provided on both sides of the switchboard. - All doors, removable covers and plates shall be provided with neoprene gaskets. All accessible live connections shall be shrouded, and it shall be possible to change individual MCCBs/MCBs/MPCBs without danger of contact with live metal. - All live parts shall be provided with phase to phase and phase to earth clearances in air of at least 25 mm and 20 mm respectively. However, for busbars the clearances specified above should be maintained even when the busbars are sleeved or insulated. All connections from the busbars up to switch / MCB /MCCB shall be fully insulated and securely bolted to minimize the risk of phase to phase and phase to earth short circuits. All busbars and jumper connections shall be of high conductivity aluminium alloy / copper of adequate size and sleeved. - All switchboards shall be provided with three phase and neutral busbars. Entire busbar system shall be insulated with colour coated PVC sleeves. Busbar sleeves shall be compliant to UL224 (Extruded insulating tubing), CE/UL certified, having fire retardant properties and working temperature of 105°C. - The cross-section of the busbars shall be uniform throughout the length of switchboard section and shall be adequately supported and braced to withstand the stresses due to the specified short circuit currents. Neutral busbar short circuit strength shall be same as main busbars. - The Cable glands shall be weatherproof Double compression type made of heavy-duty brass machine finished and nickel chrome plated of suitable size. Thickness of plating shall not be less than 10 microns. Cable glands shall conform to BS:6121. - All Cable lugs for power cables shall be Heavy duty long barrel tinned copper ring type / bimetallic solderless crimping type of suitable size. Cable lugs for control cables shall be tinned copper ring type with insulated sleeve. - All control terminals shall be of Stud type (screw drive operated) and control wiring shall be terminated with tinned copper ring type lugs with insulated sleeve. Disconnecting stud type terminal shall be provided for CT circuits. 20% spare terminal shall be provided of each type. Printed single tube ferrules marked to correspond with panel wiring diagram shall be fitted at both ends of each wire. The wire identification marking shall be in accordance with IS:375. Red Ferrules should be provided on trip circuit wiring. - All wiring shall be carried out with wires of 1.1 KV grade, stranded copper conductors. The insulation shall be halogen free and flame retardant. Power circuits shall be wired with stranded copper conductors of adequate sizes to suit the rated current, the minimum size shall be 2.5 sq. mm. Unless otherwise specified, control alarm and indication circuits shall be wired with stranded, tinned copper conductors of sizes not smaller than 1.5 sq. mm. Space heater circuits, CT and VT circuits shall be wired with stranded copper conductor of size not smaller than 2.5 sq. mm. Fill factor shall not be more than 40%. - All metallic hardware such as nuts, bolts, screws, washers etc. shall be of Hot dip galvanized as per IS standard. - All cable entries shall be located at bottom side of the panels / Junction boxes / MKs /DBs etc to prevent any possibility of water ingress into the box. All panels/Junction boxes/MKs /DBs etc shall be min. 450mm above finished floor level for cable connections - Outdoor panels/ JBs / MKs / DBs / cubicles etc. shall be completely weather-proof with a sloping extended canopy for protection against rain and providing a degree of protection of IP 55. - Busbars shall be of insulated. Busbars shall have adequate cross-section to carry the required continuous currents such that the operating temperature of the busbars does not exceed permissible temperature as per Indian standards / specification. - All busbars shall be adequately supported by non-hygroscopic, non-combustible, track resistant and high strength sheet molded compound or equivalent type polyester fiberglass molded insulator. Separate supports shall be provided for each phase and neutral busbar. If a common support is provided, anti-tracking barriers shall be provided between the supports. Insulator and barriers of inflammable material such as Hylam shall not be accepted. The busbar insulators shall be supported on the main structure - 20% spares feeders shall be considered for each type & rating. Spare modules shall be completely wired up. - All busbar joints shall be provided with high tensile steel bolts, belleville / spring washers and nuts, so as to ensure good contacts at the joints. Non-silver plated busbar joints shall be thoroughly cleaned at the jointed locations and suitable contact grease shall be applied just before making a joint. The cable entry shall be from bottom side of the switchboard and maximum operating height of the switchboard shall be limited to 1800mm - All equipment and components shall be neatly arranged and shall be easily accessible for operation and maintenance. Replacement /Maintenance of individual equipment/component shall be possible without switching off or isolating the other equipment / components. - All Switchgears panels, Distribution Boards, JBs, Fuse boards, all feeders, local push-button stations etc. shall be provided with prominent, engraved identification plates All name plates shall be of non-rusting metal or 3-ply Lamicoid, with white engraved lettering on black background. Inscription & lettering sizes shall be subject to Owner's approval - Each Inverter station shall consist of one 415V, 3 phase 4 wire LT Switchboard or Power Distribution Board (PDB). Each PDB shall be with dry type transformers of sufficient rating as per system requirement. Input to PDB transformers shall be from secondary terminal box of Inverter Duty Transformer or AC Incomer of Inverter through current limiting MCBs / MCCBs. PDB shall be comprise of transformers Incoming & outgoing MCBs/MCCBs, 415V outgoing MCBs/contactors, Overload relays/starter module and ventilation facility. PDB shall be of floor mounted, free standing, compartmentalised type with adequate space for cable entry at Inverter Station. For Indoor type PDB, degree of protection class shall be minimum IP42 and colour finish shade of PDB enclosure for interior shall be glossy white & for exterior it shall be, RAL 7035 for external and White for internal of IS: 5 and as per C5-M for outdoor and C4-M painting standard specifications for indoor application . Design of PDB shall be such that in case of non-availability of incomer supply from that Inverter, Aux. supply to other inverter shall be available (Auxiliary transformer to be fed from two inverters with suitable changeover switch) if Aux. supply shall be derived from Inverters. If Aux. supply shall be derived from any LV of IDT then no changeover switch shall be required and Aux. supply shall be derived through suitable current limiting MCCBs (with enclosure) mounted at cable box of that LV winding of IDT. - Cable termination arrangement for power cables shall be suitable for heavy duty, 1.1 kV grade, stranded aluminium conductor, PVC/ XLPE insulated, armoured / unarmoured and PVC sheathed cables. All necessary cable terminating accessories such as supporting clamps and brackets, hardware etc., shall be provided by the Bidder, to suit the final cable sizes. - Painting of all metallic enclosed electrical panels including, LT Panels, JB, DBs, MK, enclosures, etc. shall be of Shade RAL -7035 for external and White for internal and Shall be as per ISO 12944-5, corresponding to minimum C5-M specifications for outdoor equipment and C4-M specifications for indoor equipment. Unless noted otherwise, all steel structures exposed to environment would be painted to meet the requirements of corrosion category or would be galvanized to minimum 110microns - Design shall be as per Seismic Zone - V of IS 1893 - Following Diversity factor shall be considered for sizing calculations of Aux-transformers For non-continuous loads - 0.5 For all other loads – 0.8. |
| --- | --- |
|  | - Moulded Case Circuit Breakers (MCCB) / Motor Protection Circuit Breakers (MPCB) |
|  | - Moulded case circuit breakers (MCCBs) shall be provided when called for as specified. The MCCBs shall conform to the latest applicable standards. - MCCBs in AC circuits shall be of 3 pole type for 3 wire system and 4 pole type for all 3-Ph and neutral system. The ON, OFF and TRIP positions of the MCCB shall be clearly indicated and visible to the operator. Operating handle for operating MCCBs from door of board shall be provided. - MCCB shall be fixed type module, air break type, having trip free mechanism with quick make and quick break type contacts. MCCB of identical ratings shall be physically and electrically interchangeable. MCCB shall be provided with 1 NO and 1NC auxiliary contacts wired up to TB. - The instantaneous short circuit release shall be so chosen by the Supplier as to operate at a current in excess of the peak motor inrush current and a range of settings shall be provided for the Owner’s selection. - MCCB / MPCB terminals shall be shrouded and designed to receive cable lugs for cable sizes relevant to circuit ratings. Extended cable terminal arrangement for higher size cable may also be offered. - MCCB / MPCB shall have inbuilt front adjustable releases (overload & short circuit) and shall have adjustable earth fault protection unit also. The protection settings shall have suitable range to achieve the required time & current settings. LED indications shall also be provided for faults, MCCB status (on/off etc) - The MPCB’s shall be in generally similar to that of MCCB’s in all the features mentioned above. - MCCBs/MPCBs shall be provided with overload thermal release setting range of 50% to 100% of rated current and adjustable short circuit magnetic release of 5 to 10 times rated current. - The DC circuits shall be provided with DC MCCB / MCBs. - MCCBs/MPCBs shall have following accessories and features: - Shunt trip release - Auxiliary contact set of 1 NO + 1 NC - Fault signalling contact set of 1 NO + 1 NC - Insulation shields to isolate the connection between each pole - Finger protection plate to prevent accidental contact - The compartment door shall be interlocked with handle of MCCB/MPCB. - OEM supplied Interphase Barriers, shrouds, spreader terminal etc. - Miniature Circuit Breaker (MCB): Miniature circuit breaker (MCB) shall conform to IEC 898 and IS 8828. MCB shall be provided with thermo-magnetic type release for over current and short circuit protection. The MCB shall have breaking capacity not less than 10kA. MCB’s are to be mounted on DIN channel only. The operating handle shall have a clear trip indication. - Contactor, overload relay, switches, meter & instruments transformers, push button, indicating lamp etc. shall be in line with standard industrial practices and as per IS /IEC standard only and make and type shall be finalised as per system requirement during detail engineering. |

- Technical Parameters

| Sl. No. | ## Description | Unit | Requirements |
| --- | --- | --- | --- |
|  | Type | - | Floor mounted, Free standing, single/double front, compartmentalised. |
|  | Fully draw out / Semi-draw out / Fixed | - | Fixed |
|  | Installation | - | LT switchboard, PDB, LDB Indoor and for other panels installation location will be decided in detail engineering as per owners requirement |
|  | System Parameters | - |  |
|  | Main system | - | 3ph, 4 wire |
|  | Rated operational voltage | V | 415V |
|  | Impulse withstand voltage | V | As per IEC |
|  | Dry frequency withstand voltage | V | As per IEC |
|  | Earthing system | - | Solid earthing |
|  | Sheet steel thickness | mm | 2.0 |
|  | Paint shade | - | RAL 7035 for external and White for internal as per C5-M for outdoor / C4-M for indoor specifications |
|  | Busbar continuous rating | A | As per system requirement |
|  | Short time rating, (1-sec) | kA | As per maximum fault level |
|  | Incomer & Outgoing terminals |  | As per system requirements |
|  | Clearance in air - Between poles - Between pole and earth | mm mm | 25 20 |
|  | Degree of protection provided by the enclosure | - | IP42 for indoor IP 55 or Better with extended canopy for outdoor |
|  | Earth busbar size | sq.mm | As per maximum fault level |
|  | LED indication lamps provided for incoming feeder | - | Required |
|  | Space heater, illumination | - | Required |
|  | Illumination with LED lamp provided | - | Required |
|  | 6+16 A, 5 pin sockets provided | - | Required |
|  | Four pole Surge protection provided | - | Required |
|  | Shunt trip for incomer MCCB | - | Required |
|  | Multifunction meter with CTs (Accuracy class 0.5s or better) | - | Required |
|  | MCCB |  |  |
|  | - Voltage, frequency & no. of phases | - | 415 V, 50 Hz & 3 PH |
|  | - Rated operating duty | - | As per IS |
|  | - Rated ultimate breaking capacity (Icu) at 415 V, 0.25 PF | kA (rms) | As per maximum fault level |
|  | - Rated service breaking capacity (Ics) at 415 V, 0.25 PF | kA (rms) | As per maximum fault level |
|  | - Rated making current | kA (Peak) | As per maximum fault level |
|  | Releases required |  |  |
|  | - Over-load inverse time, short circuit and earth fault | Yes/No | Yes |

- Tests

- Routine tests

All routine tests shall be carried out as per applicable standards but not limited to following:

- IR test before and after HV test

- HV test

- Mechanical operations / interlocks test

- Functional tests on auxiliaries, Alarms & indications

- Type tests

Type test reports for the switchboard panel of similar rating for the following tests shall be submitted along with the Bid:

- Temperature rise

- Degree of Protection

- Short Circuit

- Salt spray test for a minimum duration of 500 hrs. (If applicable)

- Data to be furnished by vendor after award of contract

- Drawings / Documents for Approval:

- Engineering Schedule indicating list of drawings, documents, data, test certificates, manuals, etc. to be submitted by the Bidder together with dates of submissions and category of approval i.e. for approval or for reference.

- GA & Cross-sectional drawings.

- Guaranteed Technical Particulars.

- Single line diagram.

- Bill of materials indicated with make, model, type, technical specification, etc. for all equipment / accessories.

- Detailed cross-sectional drawings showing all relevant internal details of all equipment / accessories.

- Drawing showing terminal connection.

- Detailed quality assurance plan.

- Final test procedures (at shop as well as at site) and Test Set-Up.

- Design calculations (wherever necessary) to prove the adequacy of the equipment offered.

- Any other drawings / documents considered necessary.

- The manufacturer is to furnish a detailed QAP and MQAP as per standard / CEA regulations/guidance indicating the practice and procedure along with relevant supporting documents.

- Drawings / Documents for Information:

- Type test certificates valid for as per regulation for all equipment / accessories being supplied under this contract.

- Instruction Manuals.

## B5 – UPS AND UPS DISTRIBUTION BOARD

|  | UPS & UPS Distribution Board |  |
| --- | --- | --- |
|  | The design, material, construction, manufacture, performance, inspection, and testing of UPS shall comply with all latest versions of standards, statutes, regulations and safety codes in the locality where the equipment is proposed to be installed. |  |
|  | Codes & Standards |  |
|  | Codes | Description |
|  | IS 16242/ IEC 62040-3 | Uninterruptible Power Systems (UPS) |
|  | IEC 60529 | Degrees of protection provide by enclosures (IP Code) |
|  | IEC 60417 | Graphical symbols for use on equipment |
|  | IEC 61439 | Standard for low voltage switchgear and control gear assembly |
|  | IEC 60755 | General requirements for residual current operated protective devices |
|  | IEC 61000-2-2 | Electromagnetic compatibility (EMC) |
|  | IEC 61326-1 | Electrical equipment for measurement |
|  | UL 508 | Standard for Industrial Control equipment |
|  | IEC 60269-6 | Low Voltage Power Fuses |
|  | IEEE 1184 | Guide for Batteries for Uninterruptible Power Supply Systems |

|  | Design Criteria and Technical requirements - The UPS systems shall be designed to meet the auxiliary power requirements in respective Inverter stations, Sub-pooling stations and PV Plant SCADA, monitoring and Spare room Buildings (each for 1x300 and 1x200 MW). - For each SCADA control room, UPS shall have 2x 100% configuration including 2X100% battery bank.. - For each Inverter stations and each Sub pooling stations, UPS systems shall have 1 x 100% configuration. - Deleted. - During the sizing of UPS, following loads shall be considered (but not limited to). - UPS for Inverter Station - Data Logger - Fire protection and alarm system and NIFPS - CCTV - Emergency lighting - PLC - Inverter auxiliary supply (if applicable) - WMS - Inverter transformer - ICOG - Module washing system (if applicable) - Single Axis Tracker controller (Bidder to provide backup power from the UPS of inverter room as required) - Lightening Arrestor (if applicable) - UPS for Sub pooling station/MCR - Data Logger - Fire protection and alarm system - CCTV - Emergency lighting - PLC - Inverter auxiliary supply (if applicable) - WMS (if applicable) - Inverter transformer - ICOG (if applicable) & Sub pooling panel loads - Modems for ABT metering systems - Module washing system (if applicable) - Single Axis Tracker controller (Bidder to provide backup power from the UPS of inverter room as required) (if applicable) - Lightening Arrestor (if applicable) - UPS for SCADA and monitoring station - Data Logger / SCADA - Fire protection and alarm system - CCTV - Emergency lighting - PLC - PPC - WMS (if applicable) - Any other load as decided during detailed engineering - The charger shall be fed from 415V AC, 50 HZ, 3 phase, 3 wire system. Charger design shall ensure that there is no component failure due to fluctuations of input supply or loss of supply and restoration. - UPS for Inverter station / blocks and Control room shall have battery backup as per latest CEA technical standard respectively or minimum 2 hours battery backup for each battery bank whichever is higher. - Deleted. - Design temperature shall be 50 degree centigrade or as per CEA guidelines / working committee report whichever is higher. - UPS shall be sized considering 25% margin on full load requirement. Other criteria to be considered for UPS and battery sizing are - UPS load power factor shall be taken as 0.8 lagging. - UPS efficiency shall be taken as 80%. - UPS and charger design margin shall be taken 10% at 50 deg C. - IEEE-485 standard shall be followed for sizing calculation of Lead Acid Batteries and IEEE-1115 standard shall be followed for sizing calculation of Nickel- Cadmium batteries (if applicable). - For Battery sizing calculation, lowest electrolyte temperature shall be taken as minimum ambient temperature at the site location, with Temperature correction factors as per relevant standards. - Batteries aging factor shall be taken as 1.25 and design margin factor shall be taken as 1.10. - The UPS system shall include 230V AC distribution board with necessary MCBs / MCCBs. The UPS system shall be incorporated with complete circuit protection against all types of abnormal conditions which the system is likely to encounter while in service. All components, sub-assemblies & complete system, regulator, transformer, and the complete UPS, ACDB shall be subject to routine tests as per relevant standards. The UPS system offered shall be suitable for normal operation, emergency operation with required protections for IGBT, automatic synchronisation etc. Necessary contacts required for remote alarm in SCADA shall be provided. - The UPS system shall be capable of operating without D.C battery in circuit under all conditions of load and the performance of various components of UPS like inverter, charger, static switch etc. shall be guaranteed without the battery in circuit. - Control circuitry of the rectifier shall be designed in such a way that the failure of any part of the control circuitry shall not result in unsafe mode of operation of UPS and associated equipment. - The conversion of DC to AC shall be carried out by IGBT based PWM DSP control. - The batteries provided for the UPS systems shall be of Lead-acid Tubular battery. For detail specification of Battery, refer the 110V Battery and Battery charger specification. - Manual bypass switch shall be provided for isolating the UPS during maintenance. - The static switch shall be provided to perform the function of transferring UPS loads automatically in case of failure of Inverter to standby AC source. The transfer time shall be ¼ cycle maximum in synchronous mode. - The Vendor shall clearly bring out the earthing philosophy to be adopted for the UPS electronics, protective earthing (PE) and neutral earthing. The requirement of separate clean earth independent of the plant electrical system earth shall be clearly brought out. All metallic non-current carrying parts of the Panel shall be bonded together and connected to the earth bus made of GI/Cu. - Indications & Annunciation |
| --- | --- |
|  | The UPS system shall be provided with necessary meters, mimic diagram, local indication / alarm conditions. High resolution digital display unit shall be provided for continuous monitoring of the UPS operation. The control system shall operate on Windows or equivalent platform. The following operating conditions shall be annunciated. Alarm Indication: - System fault - Rectifier charger failure - Inverter failure/ faulty - Battery under voltage - End of Battery Discharge - UPS over temperature - Overload - Static transfer to stand-by - Transfer inhibited - Overload shutdown - Emergency shutdown - Battery circuit breaker / switch open - AC Main failure - AC stand-by source mains failure - AC stand-by frequency out of range - Manual bypass ON - Fan failure - Asynchronous condition - Control power failure - Any other alarm if required during detailed engineering Status Indication on Mimic: - Mains on - Rectifier on - Battery on load - Inverter on - AC Stand-by source on - Inverter on –load - Manual by-pass on - Load on static bypass. Display of measurements: - Inverter output phase-to-phase voltages - Inverter output currents - Inverter output frequency - Voltage across battery terminals - Rectifier input phase-to-phase voltages - Rectifier input currents - Active and apparent power - Power factor - DC voltage & Current - Any other display if required during detailed engineering - Remote Interface: Bidder shall consider the UPS integration with remote SCADA for monitoring of all annunciations, alarm, and metering parameters. UPS shall have RS485 port with Modbus compatibility to communicate to remote system. The Modbus card shall be either an isolated port or terminal block. The terminal block shall allow conventional twisted pair cabling for daisy chaining. |
|  | Technical requirements of UPS DB: - The UPS Distribution board is to be provided to feed the loads. The UPS DB shall be provided with single input - Multi output feeders and the same shall be decided as per system requirement. - The AC Distribution board shall be made of CRCA material with full dust, water & vermin proof arrangement. - UPS Distribution board shall be provided with High Quality MCCB, RCCB, MCB, Aluminium busbar and cables of suitable ratings. - The UPS Distribution board shall have suitable arrangement for the following: - Incoming from ACDB shall be connected to bus bar. - All MCB o/p shall be connected at Common Al Busbar. - Arrangement for disconnection of each of the inputs. - Suitable space for workability and natural cooling. - Rating of all components of UPS Distribution board shall be suitable with adequate factor of safety. - Maintenance free earthing shall be done as per the relevant standards. - Proper ventilation to be provided and designed by considering 50-degree ambient temperature. - Busbar should be shrouded / sleeved to prevent accidental contact. - Suitable markings shall be provided on the bus bar for easy identification, and cable ferrules must be fitted at the cable termination points for identification. Cable ferrules should be sunlight / UV resistive. - Fire retardancy shall follow UL94 V0 standard. - All live parts which become accessible on opening any hinged door shall be shrouded. |

- Technical Parameters

| Sl. No. | ## Description | Unit | Technical Requirements |
| --- | --- | --- | --- |
|  | General requirements |  |  |
|  | Type | - | Static Type |
|  | Power Rating at Load PF 0.8 Lagging | - | To be decided based on Load |
|  | Application | - | SCADA, Inverter station and sub pooling station |
|  | Installation /Paint shade | - | Indoor / Shade RAL 7035 for external and White for internal as per C4-M specification |
|  | Input supply | V | 415V, 1 Ø AC |
|  | Output Voltage | V | 240V, 1 Ø AC |
|  | Frequency | Hz | 50 |
|  | Current rating | - | By Bidder |
|  | AC voltage accuracy (steady state) over entire load, load PF & DC voltage range | - | 1% |
|  | Technical requirements |  |  |
|  | Range of adjustment of AC output | - | 95 to 105% |
|  | Rectifier | - | IGBT Based PWM Technology |
|  | Ripple content in DC without Battery | - | <1% |
|  | Ripple content in DC with Battery | - | <1% |
|  | Inverter | - | IGBT Based PWM Technology |
|  | AC harmonic content | - | 5% total, 3% Max for any individual |
|  | Design Ref. Ambient | o C | 50 or CEA guidelines / working committee report whichever is higher |
|  | Storage Temperature | o C | -15 to 60 |
|  | Overload capacity | - | 120% for 10 min 150% for 1 min |
|  | Battery type | - | 1X100%, Lead Acid Tubular |
|  | Battery Backup time | Hrs | As per latest CEA technical standard or minimum 2 hours battery backup for each battery bank whichever is higher |
|  | Static Transfer Switch |  | Required |
|  | Servo Controlled Voltage stabilizer |  | Required |
|  | Type of UPSDB |  | Floor/Wall mounting |
|  | Seismic Acceleration |  | 0.36g |
|  | Ingress Protection |  | IP 42 for indoor |
|  | Installation |  | indoor |

|  | TESTS - Routine tests on the complete UPS system shall be carried out as per relevant standards for each major sub-system in the UPS, viz., Rectifier, Inverters, batteries, stand-by supply etc. - Type and routine tests certificates for all components used in the UPS system shall be furnished. Tests for components shall be as per relevant standards. - BIDDER shall furnish the quality assurance plan for the equipment offered. The quality assurance plan shall include bought out components and assemblies used in the UPS system. - System tests shall be performed on the completely assembled UPS system. System tests shall include frequency regulations, Voltage regulation, current limiting feature and harmonic content tests in addition to the tests to prove the functional requirements such as synchronisation with range of adjustments, transfer of static switches for conditions of loss of square wave, overload and under voltage conditions. - Endurance test on static switches shall be performed for not less than 10 transfer / retransfer cycles at full load. - Heat run test shall be carried out on each branch of UPS including bypass (if provided) and on overall UPS system at rated load under relevant ambient conditions for a period of 8 hours. This test shall be conducted as a routine test on all UPS being supplied. |
| --- | --- |
|  | Data to be furnished by vendor after award of contract - Drawings / Documents for Approval: - Detailed schematic diagram of the UPS system showing all components - Bill of Material indicating rating & type designation of components. - General Arrangement drawing showing overall dimensions, foundation fixing details, location of various devices, mimic diagram, list of protections, annunciation and meters, cable openings, etc. - UPS and Battery Sizing Calculation - Battery room Layout - Battery Drawings/documents as specified in battery Specification - Single Line Diagram - Data sheet - Factory acceptance test - Manufacturing quality plan - Any other drawing required during detailed engineering - Drawings / Documents for information: - Type test reports on components chosen. - Quality assurance plan. - Instruction manuals. |

.

## B6 – 110V BATTERY AND BATTERY CHARGER

|  | 110V Battery and Battery Charger |
| --- | --- |
|  | 110V Battery Charger with 110V Lead-acid Tubular (OPzS) battery complete with battery racks, inter-cell and inter-tier connectors and all other accessories shall be provided as per system requirement in all 33kV sub-pooling stations. The design and engineering shall as per latest Indian standards or IEC standards. For each sub pooling substation 110V DC system shall be provided. However for inverter stations 2x100% power packs to be provided. Each set shall consist of the following: - Set of 110V Battery - 110V Float cum Boost Charger - DC Distribution Board (Compartmentalized, integral DCDB with charger is not acceptable) - DC Cables for connecting battery to charger and DCDB - Battery rack with fixing arrangements in line with specification requirement - Inter cell, Interbank and Terminal connectors in line with specification requirement |
|  | Codes & Standards |

|  | Codes | Description |
| --- | --- | --- |
|  | IEC: 60896-2 | General requirement and method of tests for Valve regulated battery |
|  | IS: 1069 | Water for Storage Battery |
|  | IS: 266 | Sulphuric Acid |
|  | IS: 6071 | Synthetic separator for Lead Acid Batteries |
|  | IEEE: 485 | Recommended practice for sizing Lead acid batteries for stationary applications |
|  | UL: 924 | Containers & Vent Plugs |
|  | UL: 1778 | Battery Enclosures |
|  | IS: 1146 | Rubber and plastic containers for lead acid storage battery |
|  | IEC 61439 | Switchgear and control-gear for voltages upto and including 1000V A.C. and 1200V D.C |
|  | IEC 60529 | Degree of protection provided by enclosures (IP Code) |
|  | IS:7098 (Part -I) | Cross linked polyethylene insulated PVC sheathed cables for working voltages up to and including 1100V |

|  | Design Criteria |
| --- | --- |
|  | Lead-acid Tubular (OPzS) battery - Batteries shall be SAN container Lead-acid tubular (OPzS) type. (Type II, High discharge performance cell as per IS 1651) - Battery shall be sized considering ten (10) hour load cycle. Battery sizing and cell selection shall be based on IEEE. While estimating battery capacities the following shall be considered: - Maximum ambient temperatures & minimum site ambient temperatures - 10% design margin - An ageing factor of 1.25 - 15% Future Load - The standard temperature used for stating cell capacity is 27deg C at a 10-hour discharge rate. The nominal voltage per cell shall be 2.0V. End voltage of cell shall be not less than 1.85V. - Battery racks / stands shall be constructed from best quality FRP. The racks shall be rigid, mechanically strong, free standing type and free from warp and twist. The completed racks shall be suitable for being bolted end to end to form continuous row. Insulators shall be provided below the legs of the stands. - Batteries shall preferably be located in the single tier arrangement. However, batteries having a complete cell weight of lower than 50 Kg could be located in the double tier arrangement. - The electrolyte shall be prepared from battery grade sulphuric acid and distilled water. - Battery containers shall be made of transparent styrene acrylo nitrile (SAN) polymer. Containers shall be robust, heat resistance, fire retardant, leak proof, non-absorbent, acid/alkaline resistant, non-bulging type and free from flaws such as wrinkles, cracks, blisters, pin holes etc. - Batteries shall have thick plates designed for maximum durability during all service conditions including high rate of discharge and rapid fluctuations of load. The tubular plate construction shall consist of high pressure cast lead alloy spines. - Transparent SAN containers shall have marked electrolyte level indicator on its body. - The separators shall maintain the electrical insulation between the plates and shall allow the electrolyte to flow freely. Separators should be suitable for continuous immersion in the electrolyte without distortion. - The cells shall be supported on FRP insulator fixed on to the FRP rack with adequate clearance between adjacent cells. - The positive and negative terminals shall be clearly marked. - Vent plug shall be provided which shall be anti-splash type. It shall allow the gases to escape freely but prevent the acid spray from the battery. - Sufficient sediment space shall be provided beneath the plates to accommodate any plate deposit, which accumulates at the bottom of the cell over a reasonable life of battery without short circuiting the plates. - The following items shall be provided for the battery. - Rack insulators - Cell insulators - Long/Short connectors - Inter row connectors (Insulated solid plated copper busbars) - Interbank connectors (Insulated solid plated copper busbars) - Vent plug - Float guide - Proper Battery take-off arrangements and shall be finalized during detail engineering as per owner requirement. - Level indicator - Fasteners (SS-304) - Cell number plates (On cells as well as on stand / rack) - Lead coated copper connectors shall be used for connectors. Bolts, nuts and washers shall be effectively lead coated to prevent corrosion. All the terminals and cells, interconnections shall be fully insulated or have insulation shrouds/covers. Connectors shall be supplied by OEM of battery cell only. - The cell terminals posts shall be provided with connector bolts and nuts, effectively coated with lead to prevent corrosion. - End take off connections from positive and negative poles of batteries shall be made by single core cables having stranding class 4 copper conductors and shall be XLPE insulated. Necessary supports and lugs (Heavy duty long barrel copper lugs) for termination of these cables on batteries shall also be supplied. All connectors and lugs shall be capable of continuously carrying specified discharge current of the respective batteries and through fault short circuit current which the battery can produce and withstand for the period declared. - Lead-coated bent copper plate, tubular copper lugs, teakwood clamp, bolts, nuts, washers, etc. shall be furnished for connection of outgoing copper conductor cables. - FRP Racks / Stands shall be free standing type, mounted on porcelain insulators. Numbering tags for each cell shall be attached on to the racks as well as on the cells. The bottom tier of the stand shall not be less than 150 mm above the floor. Wherever racks are transported in dismantled conditions, suitable match markings shall be provided to facilitate easy assembly. - Battery racks and other supporting/interconnecting accessories shall be as per layout arrangement to be approved by Owner during contract engineering stage. - Battery bank installation shall have minimum clear distance of 1.0 meter between inter row and from all side (Walls, other battery bank etc.) and installed in room with partition. Proper ventilation, eye washer, Acid proof tiles etc. shall be provided in battery room as per statutory requirements. - Following accessories shall be provided for each substation. - Electronic Syringe type Hydrometer with temperature measurement and with built in memory suitable to measure up to four set of battery banks each of 110 cells. - Digital Multimeter with measuring probes. - Acid resistant funnel. - Acid resistant jug. - Rubber apron and gloves. - Insulated Spanners- 2 sets. - Wall mounted teak wood rack/ Acid resistance rubber insulated FRP rack for above items - Lifting device for cell - The rating indicated is minimum requirement. Vendor shall carry out sizing calculation and provide required rating. Battery shall be design for ten hours back-up |
|  | DC Distribution board |
|  | - DC Distribution board shall be Indoor, Floor mounted, compartmentalised type construction. - Positive and negative bus bars in the DC switchgears shall be completely segregated from each other by sheet steel partitions. - The maximum voltage variation allowed at the load end shall be +10% to -15% at all operating conditions for both DC systems. - Short circuit withstand rating of the DCDB shall be as per system study. - DCDB shall be sheet steel enclosed and shall be dust, weather and vermin proof. Sheet Steel used shall be cold rolled and at least 2.0mm thick and properly braced to prevent wobbling. The components shall be housed in a well-ventilated sheet metal cubicle complete with input and output terminals. 20% spare feeders of each type and ratings complete in all respect shall be provided for Future use. - Suitable synthetic rubber gaskets shall be provided to make boards completely dust and vermin-proof with a degree of protection of IP42 (minimum) for indoor installation. - DBs shall have bottom entry for cables. Cable entry facilities shall be provided with removable gland plates (pre-drilled) of suitable thickness. All incoming and outgoing cables shall be terminated on suitable terminal blocks - All wiring shall be carried out with wires of 1.1 KV grade, stranded copper conductors. The insulation shall be halogen free and flame retardant. Power circuits shall be wired with stranded copper conductors of adequate sizes to suit the rated current, the minimum size shall be 2.5 sq. mm. - Unless otherwise specified, control alarm and indication circuits shall be wired with stranded, tinned copper conductors of sizes not smaller than 1.5 sq. mm. Space heater circuits etc shall be wired with stranded copper conductor of size not smaller than 2.5 sq. mm. - All control terminals shall be of Stud type (screw drive operated) and control wiring shall be terminated with tinned copper ring type lugs with insulated sleeve. Printed single tube ferrules marked to correspond with panel wiring diagram shall be fitted at both ends of each wire. The wire identification marking shall be in accordance with IS:375. Red Ferrules should be provided on trip circuit wiring. - Module details of DC Distribution board: - The incomer modules shall be MCCB controlled. Each incomer shall be provided with: - Ammeter & voltmeter - Under voltage relay with timer - Indicating lamps for ON, OFF, UNDER VOLTAGE conditions - Outgoing feeders shall be with double pole MCBs - DCDBs for sub pooling stations shall be provided with tie feeder on both sides. One of the tie feeder shall have voltmeter on bus side as well as line side and shall be provided with ammeter. All instruments shall be integrated with SCADA system. |
|  | DC System Cables (for 110V DC battery system) |
|  | - 1100V grade, single core cables with stranded Copper conductor, XLPE insulated, with PVC inner sheath, armoured and outer sheath made of FRLSH PVC compound, generally conforming to IS 7098 (for XLPE) shall be used from batteries/ battery chargers to DCDB, main DC supply to various system cabinets / panels, Switchgears etc. and for critical auxiliaries. - Voltage drop in cables between battery to DCDB and battery charger to DCDB shall be limited to 2%. Voltage drop in cables between DCDB and loads shall be limited to 3%. - Design Calculation for arriving at cable size shall be submitted for Owner’s approval. - The Cable glands shall be weather proof Double compression type made of heavy duty brass machine finished and nickel chrome plated of suitable size. Thickness of plating shall not be less than 10 micron. Cable glands shall conform to BS:6121. - All Cable lugs for power cables shall be Heavy duty Long barrel tinned copper ring type / bimetallic solderless crimping type of suitable size. Cable lugs for control cables shall be tinned copper ring type with insulated sleeve. |
|  | Battery Charger |
|  | - The float and boost battery charger shall be SMPS (Switch Mode Power Supply) type SMPS modules shall be hot swappable. It shall have N+1 redundancy. - The float cum boost charger shall be designed for supplying: - The D.C continuous load. - The float charging current of the battery. - Largest D.C motor running current, if any - 25% margin over the above loads - Supplying the boost charging current of the battery. - The SMPS Modules shall be designed for single phase or 3 phase, 50 Hz input supply. - The D.C. output voltage during float charging shall be stabilized within ± 1% of the set DC bus voltage for AC input voltage variation of ±10%, frequency variation of ± 5% and DC load variation from 0 - 100%. The voltage regulation shall be achieved by a constant voltage regulator with high frequency SMPS with intelligent control. - The float charger will be normally ON, supplying the D.C. load and at the same time trickle charging the battery. FCBC shall be suitable for float charging as well as boost charging the battery. Each battery charger shall be capable of float charging the battery supplying the station normal DC load. Design shall be such that in case the load exceeds the charger capacity, the excess load current shall be supplied by the battery - The ripple content shall be within 1% of D.C. output nominal voltage with battery disconnected. Also, in any mode of operation, the maximum harmonics (THD) in the charger input shall not exceed 5% and input power factor shall be better than 0.85. - The setting of the output D.C. bus voltage shall be adjustable between ±10% of nominal rated voltage. - All battery chargers shall be provided with Constant Voltage and Constant Current mode and facilities such as automatic voltage regulator (AVR) for both automatic and manual control of output voltage and current. A selector switch shall be provided for selecting the mode of output voltage / current control, whether automatic or manual. Means shall be provided to avoid current / voltage surges of harmful magnitude / nature which may arise during changeover from auto to manual mode or vice-versa under normal operating condition - Charger cubicles shall be sheet steel enclosed and shall be dust, weather and vermin proof. Sheet Steel used shall be cold rolled and at least 2.0mm thick and properly braced to prevent wobbling. The components shall be housed in a well-ventilated sheet metal cubicle complete with input and output terminals. - Electronic equipment shall be of modular design consisting of plug in modules in standard metallic racks with metallic card guides. Card to card wiring shall be through motherboard. The modules shall be hot-swappable to reduce MTTR (Mean Time to Repair). - Indications, controls and output voltage setting adjustments shall be on front panel. - Louvers shall be provided for ventilation backed up by fine wire mesh so that the degree of protection shall be equal to or better than IP-42 or better - All wiring shall be carried out with wires of 1.1 KV grade, stranded copper conductors. The insulation shall be halogen free and flame retardant. Power circuits shall be wired with stranded copper conductors of adequate sizes to suit the rated current, the minimum size shall be 4 sq. mm. Unless otherwise specified, control alarm and indication circuits shall be wired with stranded, tinned copper conductors of sizes not smaller than 1.5 sq. mm. Space heater circuits, etc circuits shall be wired with stranded copper conductor of size not smaller than 2.5 sq. mm. - All control terminals shall be of Stud type (screw drive operated) and control wiring shall be terminated with tinned copper ring type lugs with insulated sleeve. 20% spare terminal shall be provided of each type. Printed single tube ferrules marked to correspond with panel wiring diagram shall be fitted at both ends of each wire. The wire identification marking shall be in accordance with IS:375. Red Ferrules should be provided on trip circuit wiring - Ground terminals with isolating links shall be provided. The DC System shall be ungrounded and float with respect to the ground potential when healthy. - MCCB shall be Triple pole type for incoming supply to Battery charger, Double Pole type for outgoing supply from Battery charger. It shall be quick make, quick break, independent manual type with trip free feature. All MCCB shall have the following - Short circuit release - ON/OFF and Trip position indicators. - On, Off and Trip position potential free contacts to be integrated to SCADA - Test trip push button - Voltage rating shall be suitable for 500 volts AC/DC - Following features shall be provided in the charger: - One (1) Auto / Manual selector switch for selecting the mode of operation of the controller. - One (1) set of MCCB for AC input with suitable ratings and with trip indication for each of the charger units. - One (1) set of MCCB complete with fuse fittings for the DC output and with trip indication. - One (1) DC under voltage of the battery shall be integrated to the SCADA. - One (1) cubicle thermostatically controlled space heater suitable for 240 V AC 50 Hz, single phase shall be provided. - One (1) 240 V AC lamp for cubicle internal lighting shall be provided. - Two (2) - ON/OFF switches with MCB for space heater and internal lighting shall be provided. - Following annunciation shall be provided as minimum and shall be integrated to the SCADA - Mains AC failure - Charger over load - DC output breaker tripped - AC input breaker tripped - Battery fully discharged - Battery on boost - DC system earth fault - DC under voltage - DC Over voltage - Charger current limited protection operated - AVR Defective - SMPS module failure - Battery breaker tripped - Battery on boost In-case all above parameters as part of HMI (with local display) is also acceptable - Following analogue / digital meters shall be provided for charger to read the following measurement parameters: - AC input voltage and current - Charger input current. - DC Output current of Float/Boost Charger - DC Output voltage of Float/Boost Charger - Load voltage and current - Battery voltage - Battery current - Charge/discharge currents of the battery In-case all above parameters are available in HMI (with local display) then separate meters are not required - For remote metering and Integrated to SCADA for monitoring of the following parameters shall be provided for each Charger. 4-20 mA Transducers with dual output type to monitor the following: - DC Voltage and Current of float charger & Float cum Boost Charger - DC Voltage and Current of Battery - Battery voltage low, high and normal In case all above parameters as part of HMI (with local display) is also acceptable - All Indoor equipment, panels and cabinets (Battery Chargers) shall be pre-treated as per IS 6005 before being factory-painted with epoxy based paint shade of paint shall be RAL 7035 for external and White for internal . Corrosivity grade C4 as per ISO 12944 shall be considered for indoor equipment. Painting shall be carried out by approved process. Sufficient quantity of touch-up paint shall be furnished for application at site. - Design shall be as per Seismic Zone - V of IS 1893 |

- Technical Parameters

| Sl. No. | Item Description | Unit | Technical Requirement |
| --- | --- | --- | --- |
|  | Battery |  |  |
|  | General |  |  |
|  | Application | - | For Protection/Control system and emergency Lighting |
|  | Type of battery | - | Lead-acid Tubular (OPzS) battery |
|  | Nominal Voltage | V | 2 |
|  | Battery Capacity | AH | To be calculated by Bidder based on Duty Cycle |
|  | Number of battery banks required | No. | As per tender |
|  | Number of cells (approximate) | No. | 54 |
|  | Temperature |  |  |
|  | - Min. temp. | 0C | 10 |
|  | - Design ambient temperature | 0C | 50 |
|  | Rating |  |  |
|  | Design margin | % | 10 |
|  | Ageing factor | - | 1.25 |
|  | DC System Voltage at DC bus of the Switchboard |  |  |
|  | - Normal | V | 110 |
|  | - Maximum | V | 121 |
|  | - Minimum | V | 93.5 |
|  | End Cell Voltage (Volts / Cell) | (V/Cell) | 1.8 |
|  | Discharge Duty |  |  |
|  | Ampere Hour Capacity of Battery at min. temperature, 10 hour rate to give final end cell voltage | C10 | To be calculated by Bidder based on Duty Cycle |
|  | Layout and Construction |  |  |
|  | Tentative size of cables to connect battery to external circuit |  |  |
|  | - Type | - | XLPE |
|  | - Size | mm2 | To be submitted by Bidder |
|  | - Conductor material |  | Copper |
|  | FRP stands | Yes/ No | Yes |
|  | Miscellaneous |  |  |
|  | Tapped Cell arrangement for float cum boost charging arrangement. | Required / Not Required | Required |
|  | Dropper Diode arrangement for float cum boost charging arrangement. | Required / Not Required | Required |
|  | Battery Charger |  |  |
|  | General |  |  |
|  | Quantity required | Set | One for each system |
|  | Type (Float charger or Float-cum Boost charger) | - | Float-cum-Boost charger |
|  | Charger Technology | - | SMPS |
|  | DC System Voltage (Nominal) | V | 110 |
|  | DC System Earthing | - | Unearthed |
|  | Ambient Design Temperature | Deg. C | 50 |
|  | Battery Details |  |  |
|  | Battery capacity & no. of cells | AH | AH to be calculated by Bidder |
|  | Battery type | - | Lead-acid Tubular (OPzS) battery |
|  | Battery discharge facility | - | Required |
|  | Back up time required | Hours | 10 for each system |
|  | AC SYSTEM DATA |  |  |
|  | Supply |  |  |
|  | - Voltage | V | 415 / 230 |
|  | - Phase |  | 3 / 1 |
|  | - Frequency | Hz | 50 |
|  | - Variation in supply Voltage | % | +10% |
|  | - Variation in supply frequency | % | + 5% |
|  | Type of earthing | - | Solidly Earthed |
|  | Performance |  |  |
|  | DC voltage setting adjustment for float charger | % | +10% of nominal voltage |
|  | Voltage stabilisation for constant voltage regulator | % | +1% of set D.C voltage, with AC input variation as specified |
|  | Maximum permissible variation in DC voltage (no load to full load) | % | +1% |
|  | D.C. voltage setting adjustment for boost charging | % | 70% to 100% of max. boost charging voltage |
|  | D.C. current adjustment for boost charging | % | 30% to 100% of max. boost charging current |
|  | Current stabilisation for constant current regulator for boost charger | % | +2% |
|  | Minimum permissible power factor at rated continuous load | - | 0.85 |
|  | Permissible ripple content at rated continuous load | % | 1% (maximum) |
|  | Maximum permissible harmonics with or without battery | % | 5% |
|  | Miscellaneous |  |  |
|  | Cable entry | - | Bottom |
|  | Cable Sizes |  |  |
|  | - Battery | sq.mm | To be calculated by Bidder |
|  | - DC output | sq.mm | To be calculated by Bidder |
|  | - AC input | sq.mm | To be calculated by Bidder |
|  | Degree of protection of charger cubicle | - | IP 42 or better |
|  | Overall efficiency of charger | - | >80% |
|  | Communication Support | - | RS 485 (to be integrated with SCADA) |
|  | Communication Protocol | - | MODBUS |

- Tests

Acceptance tests shall be conducted at site on completion of installation and commissioning and immediately prior to putting the battery and charger in service.

- The tests for Lead-acid Tubular (OPzS) battery shall comprise of:

- Visual inspection

- Dimensional check

- Capacity test

- Test for voltage during discharge

- Storage test

- Internal resistance of battery

- Vendor shall carry out the capacity test on battery for the following conditions:

- For the load cycle specified.

- For 10 Hr discharge.

- The tests for SMPS shall comprise of:

- Ripple, power factor and input harmonics measurement by oscilloscope at different loads of battery charger

- Demonstration of guaranteed efficiency and power factor.

- HI Electronic controller, at 2 kV AC for one min on battery charger

- Checking of DC charger system monitoring and associated communication system

- Checking of auxiliary devices, protective devices & control equipment

- Type test report on an identical type and capacity of the battery and battery charger shall be submitted for Owner’s review. If type tests reports as per applicable standard is not availble then these Type tests shall be conducted on a minimum of one sample cell, typical and identical with the cells forming the complete battery offered (free of cost to owner). However, the tested cell shall not be included in the battery offered.

- Verification of constructional requirements.

- Verification of marking

- Verification of dimensions.

- Test for capacity

- Test for suitability of float operation

- Endurance test.

- Charge retention test

- Short circuit current and Internal resistance measurement test

- Heat run test

|  | Data to be furnished by vendor after award of contract - Drawings / Documents for Approval: - Layout drawing showing the battery room dimensions, No. of rows, overall dimensions of each row, cable termination location with dimension, cross sectional view etc. - No. of air changes recommended, - Detailed calculations for sizing of the battery DCDB and Battery charger considering various factors and the specified duty cycle. - Copies of Test Reports as specified in distribution schedule. - Schematic drawings showing main components and basic schemes. - General arrangements showing dimensions and space requirements. - DCDB and charger OGA, Schematic and wiring diagram , drawings and documents with all component details make, type shall be provided. - MQAP / QAP as per CEA Regulation - Stand / rack & & fixing arrangement, insulator drawing - O&M manual |
| --- | --- |
|  | - Drawings / Documents for information: - Battery characteristics: - Curve showing cell volts Vs. time of different discharge rates. - Curve showing cell volts Vs. time at different charging currents. - AH capacity Vs. years of service. - Capacity retention characteristic - Percentage capacity Vs Temperature - Charge current(A), Cell voltage(V) and charge quantity(% ) Vs time. - F factor (in tabulate format) - Copies of instruction manuals as per distribution schedule to cover installation, commissioning, operation and maintenance |

## B7 – LT POWER AND CONTROL CABLE

|  | LT Power and Control Cable |
| --- | --- |
|  | LT Power & control cables shall be of minimum 1100 volts grade XLPE & PVC insulated flame retardant, low smoke, FRLS / FRLSH conforming to IS 7098 part-1 & IS 1554 part-1. 1.9/3.3kV grade LT cable shall be used for interconnection between inverter-to-inverter transformers. |
|  | Codes & Standards |

|  | Codes | Description |
| --- | --- | --- |
|  | IS :1554 - I | PVC insulated (heavy duty) electric cables for working voltages upto and including 1100V. |
|  | IS: 3961 | Recommended current ratings for cables |
|  | IS: 3975 | Low carbon galvanized steel wires formed wires and tapes for armouring of cables. |
|  | IS: 5831 | PVC insulation and sheath of electrical cables. |
|  | IS:7098 (Part -I) | Cross linked polyethylene insulated PVC sheathed cables for working voltages up to and including 1100V. |
|  | IS : 3961 | Recommended current ratings for cables |
|  | IS 8130 | Conductors for insulated electrical cables and flexible cords. |
|  | IS: 10418 | Specification for drums for electric cables. |
|  | IS: 10810 | Methods of tests for cables. |
|  | ASTM-D -2843 | Standard test method for density of smoke from the burning or decomposition of plastics. |
|  | IEC-754 (Part-I) | Tests on gases evolved during combustion of electric cables. |
|  | ASTM-D-2863 | Standard method for measuring the minimum oxygen concentration to support candle like combustion of plastics. |
|  | IEEE-383 | Standard for type test of Class IE Electric Cables |

|  | General Requirements of LT Power Cables - 1.1 KV grade XLPE power cables shall have compacted aluminium/ copper conductor, XLPE insulated, PVC inner-sheathed (as applicable), armoured FRLS. PVC outer-sheathed conforming to IS:7098. (Part-I). Cables which are directly buried shall be armoured. However, in case of unarmored cable, adequate mechanical protection shall be ensured by the bidder. HDPE Outer sheath (ST-7) with FRLS and UV Resistant property as per IEC 60502-1 standards shall also be acceptable - The cables shall be suitable for laying on racks, in ducts, trenches, conduits and underground (buried) installation with chances of flooding by water. - If cables are to be laid underground, laying shall be as per latest relevant IS code. Cables if required to be buried in ground will be provided with special protection either through PE/LS sheath/Jacket considering soil with saline water. - All cables shall be flame retardant (FRLS) type designed to withstand all mechanical, electrical and thermal stresses developed under steady state and transient operating conditions as specified elsewhere in this specification. - Copper/aluminium conductor used in power cables shall have tensile strength as per relevant standards. Conductors shall be stranded. - The cables specifications / design shall be suitably selected as per laying final philosophy/ methodology decided during detail engineering by the Bidder considering the site environmental conditions etc. Bidder shall submit the final specification with methodology for Owner’s Approval - XLPE insulation shall be suitable for a continuous conductor temperature of 90 deg. C and short circuit conductor temperature of 250 deg C. for duration of one second - For 3 Phase, 4 Wire power system, Neutral conductor size shall be of same size as the phase conductors’ size. Half neutral shall not be acceptable. - LT cable maximum voltage drop shall be limited to 3% of rated voltage. 1.9/3.3kV grade LT cable shall be used for interconnection between inverter to inverter transformer. - For single core armoured cables, armouring shall be of copper/aluminium wires/ formed wires. For multicore armoured cables, armouring shall be of galvanised steel as follows: Calculated nominal dia. of cable under armour; Size and Type of armour. Upto 13 mm; 1.4mm dia GS wire. Above 13 & upto 25mm; 0.8 mm thick GS formed wire / 1.6 mm dia GS wire. Above 25 & upto 40 mm; 0.8mm thick GS formed wire / 2.0mm dia GS wire. Above 40 & upto 55mm; 1.4 mm thick GS formed wire /2.5mm dia GS wire. Above 55 & upto 70 mm; 1.4mm thick GS formed wire / 3.15mm dia GS wire. Above 70mm; 1.4 mm thick GS formed wire / 4.0 mm dia GS wire. - The aluminium used for armouring shall be of H4 grade as per IS: 8130. Copper / aluminium conductor shall be of electrolytic grade. - The gap between armour wires / formed wires shall not exceed one armour wire / formed wire space and there shall be no cross over / over-riding of armour wire / formed wire. The minimum area of coverage of armouring shall be 90%. The breaking load of armour joint shall not be less than 95% of that of armour wire / formed wire. Zinc rich paint shall be applied on armour joint surface of GS wire / formed wire. - Outer sheath shall be of PVC as per IS: 5831 & black in colour for power cables. In addition to meeting all the requirements of Indian standards referred to, outer sheath of all the cables shall have the following FRLS/as per regulation properties. - Oxygen index of min. 29 (as per IS 10810 Part-58) - Acid gas emission of max. 20% (as per IEC-754-I) - Smoke density rating shall not be more than 60 % (as per ASTMD-2843) - Temperature index of minimum 250C when tested as per IS 10810 Part-64Acid gas emission of max. 20% (as per IEC-754-I) - Average light transmission of 40% minimum when tested as per IS 10810 Part-63 - Flammability requirements as per IS 10810 Parts-53 and 62 - Flame retardant requirements as per IS 10810 Part-61 - Halogen content requirements as per IEC 60754 - Smoke density rating shall not be more than 60 % (as per ASTMD-2843) - Marking of cables shall be as specified in Cabling system section. - All cables shall meet the fire resistance requirement as per IEEE - 383 with cable installations made in accordance with 'Flammability Test' and as per Category-B of IEC 332 Part -3. - Allowable tolerances on the overall diameter of the cables shall be +\-2 mm maximum, over the declared value in the technical data sheets. Repaired cables shall not be accepted. - All the cables (Power and control) shall be protected against fungus, rodent and termite attack. Necessary chemicals shall be added into the PVC compound of the outer sheath. The sheath shall be resistant to saline water, UV radiation, fungus, etc - All LT cables shall be of minimum 1100 V grade, single/multi-core, stranded aluminium conductor, extruded XLPE insulated (hot water cured), with extruded PVC inner sheath (Type ST-2), armoured and overall sheath with extruded Flame-Retardant Low Smoke (FRLS)/ FRLSH PVC compound (Type ST-2), however cable for Inverter to Inverter transformer shall be of minimum 1.9/3.3KV grade. These cables shall conform to IS-7098-Part-I . All the cables shall be protected against Fungus, rodent and termite attack. Necessary chemicals shall be added into the outer sheath compound of the outer sheath. The sheath shall be resistant to saline water, UV radiation, fungus, etc. - All necessary cable terminating accessories such as supporting clamps and brackets, hardware etc., shall be provided by the Bidder, to suit the final cable sizes and shall be GI as per standard. All Cable lugs for power cables shall be Heavy duty long barrel tinned copper ring type / bimetallic solderless crimping type of suitable size conforming to IS:8309. Cable lugs for control cables shall be tinned copper ring type with insulated / sleeved. - Water swellable tape shall be provided for all cables if laid underground. - Double compression type Cable glands made of heavy-duty brass machine finished and nickel chrome plated shall be provided for cable glanding. Thickness of nickel plating shall not be less than 10 microns. Cable glands shall conform to BS:6121 - Maximum fault level shall be calculated considering PSS-2 400 KV Bus as infinite Grid / Bus. Time duration for Short circuit withstand capability shall be as under : a) Minimum 0.90 second for 3.3 KV cable b) Minimum 1.0 second for 1.1 KV cable. - For Power cable joint shall only be permitted if single cable length as per OEM manufacturing capability does not meet the requirement. |
| --- | --- |
|  | - Cable selection & sizing: The cable shall be able to carry the full load current of the circuit continuously under the specified ambient temperature. Permissible voltage drop limits under steady state/transient state as applicable. Voltage drop shall be limited to 3% of rated voltage. For sizing of all 1.1 KV LT cables following conditions shall be collectively complied. This is irrespective of cable laying methodology selected. - Additional 5.0 % Ampacity margin shall be considered. - Cable Rating in duct shall be considered. - All Power Cables are to be laid with minimum spacing of 2D between the cables edges (and NOT center to center of cables). “D” is diameter to cable. - Rating factors of air and ground temperatures, depth of laying, variation in thermal resistivity of soil, various groupings shall be considered as 1.0 - Fault level withstand capacity shall be as per tender conditions - Power Loss shall be within limits as per tender conditions. - Voltage drop shall be within limits as per tender conditions. |
|  | - Illustration for sizing of Cables: 1; Current Rating Requirement of equipment / system. (full load current of the circuit continuously under the specified ambient temperature); =; 308 Amp. 2; Additional Margin of 5%; =; 15.40 Amp. 3; Total Ampacity to be considered; =; 323.4 Amp. 4; Cable Rating of 3C x 400 Sq.mm, Aluminum, XLPE LT cable in duct (Ref IS 3961); =; 356 Amp. 5; Minimum Cable size to be provided to comply ampacity requirement.; =; 400 Sq.mm.. 6; Cable sizing calculation for Fault level withstand capacity as per tender conditions.; =; As per calculations. 7; Cable sizing calculation for Power Loss as per tender conditions.; =; As per calculations. 8; Cable sizing calculation for Voltage drop as per tender conditions.; =; As per calculations. 9; Final cable size to be provided shall be highest of Sr No 5 to 8; =. - Cable lengths shall be considered in such a way that straight through cable joints are avoided. Cables shall be armoured type if laid directly buried. Cable shall be capable of laying in underground soil with saline water in case of laying methodology selected is under ground. - The bending radii for various types of cables shall be as pe cable manufacturer recommendations. - Inverters to IDT 3.3 KV AC cables shall be design based on followings ( All conditions shall be collectively complied) : - NO Additional Ampacity margin shall be considered. - All Cables are to be laid with minimum spacing of 2D between the cable edges (and NOT center to center of cables). “D” is diameter to cable. - Total Rating factor of air and ground temperatures, depth of laying, variation in thermal resistivity of soil, various groupings shall be considered as 0.8 irrespective of cable laying methodology. - Fault level withstand capacity with duration not less than 0.9 Sec shall be as per tender conditions - Power Loss shall be within limits as per tender conditions. - Voltage drop shall be within limits as per tender conditions - Final cable size to be provided shall be highest of Sr No 3 to 6 |
|  | General Requirements of Control Cables - 1.1 KV Grade Control Cables shall have stranded copper conductor and shall be multicore PVC insulated, PVC inner sheathed, armoured, FRLSH PVC outer sheathed conforming to IS: 1554. (Part-I). - The cables shall be suitable for laying on racks, in ducts, trenches, conduits and underground (buried) installation with chances of flooding by water. - All cables shall be flame retardant, low smoke (FRLSH) designed to withstand all mechanical, electrical and thermal stresses developed under steady state and transient operating conditions as specified elsewhere in this specification. - Outer sheath shall be of PVC as per IS: 5831 & grey in colour for control cables. In addition to meeting all the requirements of Indian standards referred to, outer sheath of all the cables shall have the following FRLSH/as per regulation properties. - Oxygen index of min. 29 (as per IS 10810 Part-58). - Temperature index of minimum 250C when tested as per IS 10810 Part-64 - Acid gas emission of max. 20% (as per IEC-754-I). - Smoke density rating shall not be more than 60 % (as per ASTMD-2843). - Average light transmission of 40% minimum when tested as per IS 10810 Part-63 - Flammability requirements as per IS 10810 Parts-53 and 62 - Flame retardant requirements as per IS 10810 Part-61. - Halogen content requirements as per IEC 60754 - Smoke density rating shall not be more than 60 % (as per ASTMD-2843) - Cores of the control cables shall be identified by colouring of insulation. Following colour scheme shall be adopted: - 1 core - Red, Black, Yellow or Blue - 2 core - Red & Black - 3 core - Red, Yellow & Blue - 4 core - Red, Yellow, Blue and Black - For control cables having more than 5 cores, core identification shall be done by numbering the insulation of cores sequentially, starting by number 1 in the inner layer (e.g. say for 10 core cable, core numbering shall be from 1 to 10). - The Cable glands shall be weatherproof Double compression type made of heavy duty brass machine finished and nickel chrome plated of suitable size. Thickness of Nickel plating shall not be less than 10 micron. Cable glands shall conform to BS:6121. For flame proof equipment cable glands shall be of flame proof type.. All lugs shall be Ring type tinned copper with insulated/sleeved only. - No Joints shall be permitted in any of the control cables. - Water swellable tape shall be provided for all cables if laid underground. - While preparing cable schedules for control / protection purpose following shall be ensured: - Separate cables shall be used for AC and DC circuits - For different cores of CT and VT, separate cables shall be used - Two separate cables shall be used from DC Source-I & Source-II to each control / relay panel, each 33 KV board, SCADA, server, etc. for main & redundant control supply and Auxiliary supply |
|  | - Cable selection & sizing: Control cables shall be sized based on the following considerations: - The minimum conductor cross-section shall be 1.5 sq.mm. - The minimum number of spare cores in control cables shall be as follows: No. of cores in cable; Min. No. of spare cores. 3C, 4C; 1. 5C, 7C; 2. 10C & above; 4. |
|  | - Current transformer leads shall be checked for lead burden, VA capacity and knee point voltage. In case 2.5 mm2 Copper Conductor is not adequate, conductor of 4 mm2 cross section or higher shall be used. Voltage transformer leads shall be checked for voltage drop which shall be limited to within 1% for all cases other than tariff metering. For tariff metering the voltage drop shall be limited to 0.2%. In case the voltage drop with 2.5 sq.mm copper conductor exceeds this value, higher conductor sizes shall be used - Maximum no of cores (including spare cores) of Control cable shall not be more than 14 Cores |

- Technical Parameters

- The 1.1KV grade XLPE Power Cables shall comply with the particulars indicated below:

| Sl. No. | ## Description | Unit | Requirements |
| --- | --- | --- | --- |
| 1.0 | General Requirements |  |  |
| 1.1 | Voltage Grade | kV | Minimum 1.1 |
| 1.2 | Core | - | Single, Multi |
| 1.3 | Conductor Material | - | Copper – Cable size upto 6sq.mm Aluminium - Cable size above 6sq.mm |
| 1.4 | Insulation | - | XLPE |
| 1.5 | Inner Sheath | - | Extruded PVC Compound (ST-2 for PVC Insulation) |
| 1.6 | Armouring | - | Galvanized steel round wire/ galvanized steel strip |
| 1.7 | Outer Sheath | - | Extruded FRLS PVC Compound (ST-2 for PVC Insulation) |
| 1.8 | Maximum Conductor temperature | - |  |
|  | - Rated | o C | 90 |
|  | - During Short Circuit | o C | 250 |
| 2.0 | System details | - |  |
| 2.1 | Nominal power system voltage | V | 415 |
| 2.2 | Maximum system voltage for continuous operation | kV | 1.1 |
| 2.3 | System neutral earthing | - | As per system requirements |
| 2.4 | Design Ambient Temperature | o C | 50 |

- The 1.1KV grade PVC Control Cables shall comply with the particulars indicated below:

| Sl. No. | ## Description | Unit | Requirements |
| --- | --- | --- | --- |
| 1.0 | General Requirements |  |  |
| 1.1 | Voltage Grade | kV | Minimum 1.1 |
| 1.2 | Core | - | Multi |
| 1.3 | Conductor Material | - | Copper |
| 1.4 | Insulation | - | Extruded PVC |
| 1.5 | Inner Sheath | - | Extruded PVC Compound (ST-1 for PVC Insulation ) |
| 1.6 | Armouring | - | Galvanized steel round wire/ galvanized steel strip |
| 1.7 | Outer Sheath | - | Extruded FRLSH PVC Compound (ST-1 for PVC Insulation) |
| 2.0 | System details | - |  |
| 2.1 | Nominal power system voltage | V | 415 |
| 2.2 | Maximum system voltage for continuous operation | kV | 1.1 |
| 2.3 | System neutral earthing | - | As per system requirements |
| 2.4 | Design Ambient Temperature | o C | 50 |

- The 1.9 /3.3 KV grade XLPE Power Cables shall comply with the particulars indicated below:

| Sl. No. | ## Description | Unit | Requirements |
| --- | --- | --- | --- |
| 1.0 | General Requirements |  |  |
| 1.1 | Voltage Grade | kV | 1.9 / 3.3 |
| 1.2 | Core | - | As per system requirements |
| 1.3 | Conductor Material | - | Copper / Aluminium - Cable size as per system requirement |
| 1.4 | Insulation | - | XLPE |
| 1.5 | Inner Sheath | - | Extruded PVC Compound (ST-2 for PVC Insulation) |
| 1.6 | Armouring | - | Galvanized steel round wire/ galvanized steel strip for Multi core cables and copper / aluminum flat/ formed flat for single core cables |
| 1.7 | Outer Sheath | - | Extruded FRLS PVC Compound (ST-2 for PVC Insulation) |
| 1.8 | Maximum Conductor temperature | - |  |
|  | - Rated | o C | 90 |
|  | - During Short Circuit | o C | 250 |
| 2.0 | System details | - |  |
| 2.1 | Nominal power system voltage | V | As per system requirements |
| 2.2 | Maximum system voltage for continuous operation | kV | 1.9/3.3 |
| 2.3 | System neutral earthing | - | As per system requirements |
| 2.4 | Design Ambient Temperature | o C | 50 |

|  | Tests - Cables shall be subjected to routine and acceptance tests as per IS-7098 (Part-1). Acceptance tests and FRLS/as per CEA regulation tests as specified shall be conducted on cables and same shall be witnessed by the Purchaser. The FRLS/as per regulation tests shall be carried out on one cable of every batch of compound used. Test certificates for routine, acceptance and special tests shall be furnished by the Bidder for review and approval. Charges for these shall be deemed to be included in the equipment price. - All equipment to be supplied shall be of type tested quality. Certified copies of reports of type tests conforming to IS-7098 (Part-1) carried out on similar type and rating of cables (offered under this contract) shall be furnished to the Purchaser for review and approval. Type tests shall also include anti rodent and anti-termite test. The tests should have been either conducted at on independent laboratory or should have been witnessed by a client. In case the bidder is not able to submit report of the type test(s) conducted, or in case the type test report(s) are not found to be meeting the Specification requirements, the bidder shall conduct all such tests under this contract, free of cost to the Owner and submit the reports for approval - Acceptance tests as per IS standard and approved QAP shall be carried out on each type and size of the cables on the cable drums selected at random as per following sampling plan: Sl. No.; No. of drums in the lot; No. of drums to be taken as sample. 1.; Upto 50; 2. 2.; 51 to 100; 5. 3.; 101 to 300; 13. 4.; 301 to 500; 20. - Following Special Tests shall be conducted at factory in presence of Owner / Owners representative - Oxygen index test as per IS 10810 Part-58 - Temperature index test as per IS 10810 Part-64 - Acid gas generation test as per IS 10810 Part-59 - Smoke generation test as per IS 10810 Part-63 - Flammability tests as per IS 10810 Parts-53 and 62 - Flame retardant test as per IS 10810 Part-61 |
| --- | --- |
|  | Data to be furnished by vendor after award of contract - Drawings / Documents for Approval: - Design basis report - Cable sizing calculation - Completely filled-in Data Sheets and Schedules. - Technical particulars of cable cross sectional drawing, MQAP, FQAP, QA Plan (as per CEA regulation) and technical catalogues. - Estimated weight of cables and cable drums. - Experience list where cables of similar rating and sizes have been installed and are in satisfactory operation. - Type test certificates/reports for the equipment covered in the specification. - Any other drawings/documents considered necessary |
|  | - Drawings / Documents for information: - Continuous current rating of the cable - General technical data - Construction details including type of material used and thickness of each material for each type of cable in a tabular form. - Instruction Manuals - Type/Routine test certificates for all types of cables included in the order and special tests on FRLS/ cables in line with applicable standard. - All detailed catalogues and literature of Cables supplied |

## B8 - 33KV POWER CABLES

|  | 33kV Power Cables |
| --- | --- |
|  | The design and engineering shall as per latest Indian standards or IEC standards. |
|  | Codes & Standards |

|  | Codes | Description |
| --- | --- | --- |
|  | IS 7098 | Cross linked polyethylene insulated PVC sheathed cable for (Part -II) working voltage from 3.3KV up to & including 33 KV |
|  | IS 3961/ IEC 60287 | Recommended current ratings for cables |
|  | IS 3975 | Low Carbon Galvanized steel wires formed wires and tapes for armouring of cables. |
|  | IS 5831 | PVC insulation and sheath of electrical cables. |
|  | IS 8130 | Conductors for insulated electrical cables and flexible cords. |
|  | ASTM-D -2843 | Standard test method for density of smoke from the burning or decomposition of plastics. |
|  | ASTM-D-2863 | Standard method for measuring the minimum oxygen concentration to support candle like combustion of plastics. |
|  | IS 10810 | Methods of tests for cables. |
|  | IEC-754 (Part-I) | Tests on gases evolved during combustion of electric cables. |
|  | IEEE-383 | Standard for type test of Class IE Electric Cables |
|  | IEC-332 Part-3 | Tests on electric cables under fire conditions. Tests on bunched wires or cables (Category-B). |
|  | IS: 10418 | Specification for drums for electric cables. |

|  | General and Installation Requirements - The cable shall be 19/33kV Grade, high conductivity stranded compacted circular aluminium conductor, Three cores, XLPE insulated, Inner PVC ST2 sheathed, metallic screened suitable for carrying the system earth fault current, conductor and insulation screened galvanized steel strip armoured with overall separate extruded PVC ST2 outer sheath, FLRS/ FRLSH conforming to IS:7098 (part-II)-1985 and its latest amendments. HDPE Outer sheath (ST-7) with FRLS and UV Resistant property as per IEC 60502-1 standards shall also be acceptable. - The insulation of each core and outer and inner sheath, shall comply with the IS: 5831. The manufacturing process shall ensure that insulation shall be free from voids. The insulation shall withstand mechanical and thermal stresses under steady state and transient operating conditions. - Method of curing for XLPE insulation shall be gas/steam curing. Conductor screen and insulation screen shall both be of extruded semi-conducting compound and shall be applied with XLPE insulation in one operation through triple extrusion. - To confine electrical field to the insulation, insulation screening consisting of two parts, namely metallic (non- magnetic) and non-metallic (semi conducting) shall be provided. The non-metallic semi-conducting shield shall be put over the insulation of each core. The insulation shield shall be extruded in the same operation as the conductor shield and the Insulation by triple extrusion process. The insulation shield shall be bonded and Strippable, on adequate heat-treatment. Metallic shield shall be provided over non-metallic portion as per provision of clause 12.4 of IS: 7098 (Part- 3)/ 1985 and amendment thereof. - The cables specifications / design shall be suitably selected as per final laying philosophy/ methodology decided during detail engineering by the Bidder considering the site environmental conditions etc. Bidder shall submit the final specification with methodology for Owner’s Approval. - The sheath shall be suitable to withstand the operating conditions and the desired temperature rating of the cable. It shall be of adequate thickness, consistent quality and free from all defects. - All the armouring shall be hot dip galvanized steel strip. The dimensions of steel strip shall be as per table 4 of IS:7098 (Part-II)/1985 and its latest amendment and strip shall conform to latest provisions of IS: 3975 -1988 and amendment thereof. - Extruded PVC outer sheath of type ST-2 as per IS: 5831/1984 and its latest amendment shall be applied over armouring with suitable additive to prevent attack by rodent and termite and Its thickness shall be in accordance with clause -17.32 of IS:7098 (Part-III)/1985 and latest amendment thereof. Alternatively, HDPE Outer sheath (ST-7) with UV Resistant property as per IEC 60502-2 standards shall also be acceptable. All the cables shall be protected against Fungus, rodent and termite attack. Necessary chemicals shall be added into the outer sheath compound of the outer sheath. The sheath shall be resistant to saline water, UV radiation, fungus, etc. - Water swellable tape shall be provided for all cables if laid underground. - The construction of cable shall have suitable PVC fillers laid up with insulated cores to provide substantially circular cross section before the inner sheath is applied. The fillers shall be suitable for operating temperature of the cable and compatible with the insulating material. - Outer sheath shall be of PVC as per IS: 5831 & black in colour for power cables. In addition to meeting all the requirements of Indian standards referred to, outer sheath of all the cables shall have the following FRLS. - Oxygen index of min. 29 (as per IS 10810 Part-58). - Acid gas emission of max. 20% (as per IEC-754-I). - Smoke density rating shall not be more than 60 % (as per ASTMD-2843). - Temperature index of minimum 250 degC when tested as per IS 10810 Part-64 - Average light transmission of 40% minimum when tested as per IS 10810 Part-63 (average smoke density is maximum 60%) - Flame test requirements as per IS 10810 Parts-53 and 62 - Flame retardant test requirements as per IS 10810 Part-61 - Halogen content requirements as per IEC 60754 - Smoke density rating shall not be more than 60 % (as per ASTMD-2843) - Marking of cables shall be as specified in tender and in Cabling system section. - All cables shall meet the fire resistance requirement as per IEEE - 383 with cable installations made in accordance with 'Flammability Test' and as per Category-B of IEC 332 Part -3 - Allowable tolerances on the overall diameter of the cables shall be +\-2 mm maximum, over the declared value in the technical data sheets. Repaired cables shall not be accepted. - All materials used in the manufacture of cable shall be new, unused and of finest quality. All materials shall comply with the applicable provisions of the tests of the specification, IS, Indian Electricity Rules, Indian Elect. Act and any other applicable statutory provisions, rules and regulations. - The PVC material used in the manufacture of cable shall be of reputed make. No recycling of the PVC is permitted. The purchaser reserves the right to ask for documentary proof of the purchase of various materials to be used for the manufacture of cable and to check that manufacturer is complying with quality control. - Maximum fault level shall be calculated considering PSS-2 400 KV Bus as infinite Grid / Bus. Short circuit ratings of various sizes cable calculated for duration of one second at maximum temperature of 250º C and shall be provided by vendor in GTP. - Cores of the cables of upto 3 cores shall be identified by colouring of insulation or by providing coloured tapes helically over the cores with Red, Yellow & Blue colours. - The cables shall be suitable for being installed directly in the ground, in the pipes or in the cable trays/trenches. The cables shall therefore be suitable for satisfactory operation under the tropical climatic conditions listed in the relevant clause. - Only terminal cable joints shall be accepted. No cable joint to join two cable ends shall be accepted, except if single cable length as per OEM manufacturing capability does not meet the requirement - Cable installations shall be as per latest IS 1255. Packing and marking shall be as per clause No. 18 of IS 7098 (part I)/1988 amended up to date. - Cable identification system - In addition to manufacturer’s identification on cables as per IS, following marking shall also be embossed on the outer sheath at an interval of three 3) meter throughout the length of cables. - Owner: GIPCL - BIS mark - Manufacturer’s name and or trade mark. - Year of manufacture - Cable code - Type of cable and voltage class. - Screen Fault current _ _ _KA for _ _ _ Sec. (Value of current & time shall be indicated) (If applicable) - Fault current _ _ _KA for _ _ _ Sec. (Value of current & time shall be indicated)Nominal cross section area of conductor and no. of cores. - Progressive sequential length making (at every meter). - Cables shall be marked as having FRLS / actual specification outer sheath at every three (3) meters. - The embossing shall be progressive, automatic, in line and marking shall be legible and indelible. - Three core 19/33 kV earthed grade, cables shall constitute the following: - Circular stranded and compacted aluminium conductor - Extruded semi conducting compound as conductor screen - Extruded XLPE insulation - Extruded semi conducting compound as insulation screen - Copper tape as metallic screen for each core - Semi conducting water swellable tape with minimum 20% overlap - Extruded PVC inner sheath - Galvanized steel formed wire - Extruded FRLS PVC outer sheath or HDPE outer sheath - Core identification shall be color coded (R,Y,B) - Bending Radius: to be specified by OEM - Cables Laying and Fitting Accessories - Cables inside the Sub pooling station / Switchgear area shall be laid in Galvanized Cable Trays mounted on GI steel supports, in constructed trenches with RCC raft and brick sidewalls and provided with removable RCC covers. Ladder type GI cable tray with top cover and all fittings and accessories like coupler plates, bolts, nuts, washers, brackets, elbows, bends, reducers, tees, crosses, strap, hook etc shall be provided. Proper GI support system shall be provided for cable tray. - Power cable shall be laid on separate tiers in line with approved guidelines/ drawings. The laying of different voltage grade cables shall be on different tiers according to the voltage grade of the cables. - All End termination kits, jointing kits with all required accessories and hardware required for 33kV cable terminations at both ends (including 33kV Transmission line) is in scope of Bidder. Cable end termination kit & jointing kit (if unavoidable) shall be of approved make & shall be installed by OEM certified jointer. - Each 33KV Transmission Line - to 400/33/33KV (PSS-2) shall be of XLPE armoured cables. For PEB-3 (having maximum evacuation capacity of 300 MW), minimum 3 no’s of spare cables (of highest rating) shall be provided. Cables shall be laid in such a way that same can be used for any bays of PEB-3 of PSS-2 and any associated 33 KV panels of Inverter stations / Sub pooling stations. Details shall be finalised during detail engineering as per Owner’s requirement and without any financially implication to the Owner. For PEB-4 (having maximum evacuation capacity of 200 MW), minimum 2 no’s of spare cables (of highest rating) shall be provided. Cables shall be laid in such a way that same can be used for any bays of PEB-4 of PSS-2 and any associated 33 KV panels of Inverter stations / Sub pooling stations. Details shall be finalised during detail engineering as per Owner’s requirement and without any financially implication to the Owner. 33 KV Transmission lines from PSS-2 to periphery of solar plant shall be laid (underground and or above ground) in the allocated cable corridor. However, in case of any additional cable corridor requirement, same shall be managed by SPD from the land allocated to the SPD. Cable pits shall be provided for additional looping of cables. (Details shall be finalized during detail engineering). - Cable tray shall be fabricated out of mild steel sheets with min thickness of 2 mm and for coupler plates it shall be 3 mm thick. Material of Cable tray and all its fittings and accessories shall be Hot dip Galvanized as per IS standard. - Suitable size clamps with all fixing GI accessories shall be provided for clamping of multicore cables at every 5 meters interval. Die cast Aluminum or Fibre glass or Nylon Trefoil clamps with all fixing GI accessories shall be provided for single core cables. Trefoil clamps shall be provided at distance of every 2 meters and on either side of bends. Control cables shall be bunched, clamped and tied with self-locking type nylon cable ties with de interlocking facility to keep them in position. - Cable drums shall be unloaded, handled, stored and laid as per OEM guidelines or as per relevant IS standards. Suitable jacks or on cable wheels shall be used to unreeling the cables. All possible care shall be taken during unreeling and laying to avoid damage due to twist, kink or sharp bends. Ground rollers shall be used at every 2 meter interval for cable laying to avoid cable touching ground. - Suitable clearances shall be maintained between HT power-LT Power-Control cable laying in line with IS standard. Required length of cable for HT straight through joints shall be kept at each end location for future use. - The cable passing through openings in the cable trenches/ road /wall /floor/cable tunnel/ cable culvert shall be laid in the GI pipe /HDPE/ Hume Pipe of approved make. All opening/ entry of cables shall be provided with fire stop sealing. - All cable/wires shall be provided with Punched Aluminium tags only on both sides of a wall or floor crossing, on each duct/conduit entry / exit, and at every 10 meters in cable tray/trench runs. The marking on tags shall be done with good quality letter and number ferrules of proper sizes so that the cables can be identified easily. Suitable cable tray marking shall be provided. Cross ferruling shall be provided for each control cable cores. |
| --- | --- |
|  | Design Criteria The HT 33kV power cables shall be sized based on current carrying capacity, short circuit rating and permissible power loss as per specified under relevant performance guarantee clauses. Cable shall be capable of laying in underground soil with saline water. |
|  | Current carrying capacity: The cable shall be able to carry the full load current of the circuit continuously under the specified ambient temperature. For sizing of all cables following conditions shall be collectively complied. This is irrespective of cable laying methodology selected. - Additional 5.0 % Ampacity margin shall be considered. - Cable Rating in duct shall be considered. - All Power Cables are to be laid with minimum spacing of 2D between the cables edges (and NOT center to center of cables). “D” is diameter to cable. - Rating factors of air and ground temperatures, depth of laying, variation in thermal resistivity of soil, various groupings shall be considered as 1.0 - Fault level withstand capacity shall be as per tender conditions - Power Loss shall be within limits as per tender conditions. |
|  | Short circuit rating: For all HT power cables, Maximum fault level shall be calculated considering PSS-2 400 KV Bus as infinite Grid / Bus with duration of 1 sec.. |
|  | Permissible power loss: The power loss in HT cables shall be limited such that overall plant AC ohmic loss shall be within permissible limit as specified under relevant performance guarantee clauses. |

- Illustration for sizing of Cables:

| 1 | Current Rating Requirement of equipment / system. (full load current of the circuit continuously under the specified ambient temperature) | = | 308 Amp |
| --- | --- | --- | --- |
| 2 | Additional Margin of 5% | = | 15.40 Amp |
| 3 | Total Ampacity to be considered | = | 323.4 Amp |
| 4 | Cable Rating of 3C x 400 Sq.mm, Aluminum, XLPE cable in duct (Ref IS 3961) | = | 361 Amp |
| 5 | Minimum Cable size to be provided to comply ampacity requirement. | = | 400 Sq.mm. |
| 6 | Cable sizing calculation for Fault level withstand capacity as per tender conditions. | = | As per calculations |
| 7 | Cable sizing calculation for Power Loss as per tender conditions. | = | As per calculations |
| 8 | Cable sizing calculation for Voltage drop as per tender conditions. | = | As per calculations |
| 9 | Final cable size to be provided shall be highest of Sr No 5 to 8 | = |  |

- Technical Parameters

| Sl. No. | ## Description | Unit | Requirements |
| --- | --- | --- | --- |
|  | General requirements |  |  |
|  | Voltage Grade | kV | 33 kV |
|  | Core | - | Multi |
|  | Conductor Material | - | Aluminium as per applicable standards and codes |
|  | Conductor screen | - | Extruded semi conducting compound |
|  | Insulation | - | Extruded XLPE |
|  | Insulation screen | - | Extruded semi conducting compound with metallic tape screen over it |
|  | Inner Sheath | - | PVC Compound (ST-2) |
|  | Armouring | - | Galvanized steel strip / galvanized steel round wires |
|  | Outer Sheath | - | FRLS/FRLSH PVC compound (ST-2) HDPE Outer sheath (ST-7) with UV Resistant property as per IEC 60502-2 standards shall also be acceptable. |
|  | Cross Sectional area of conductor |  | Shall be as per design calculation and no negative tolerances is permitted |
|  | System Details |  |  |
|  | Nominal Power System Voltage | kV | 33 |
|  | Maximum System Voltage | kV | 36 |
|  | System Neutral Earthing | - | As per system requirement |
|  | Design Ambient Temperature | o C | 50 |
|  | FRLS/FRLSH PVC outer sheath required | Yes / No | Yes |
|  | Short circuit fault current capability for 1 sec | kA | Maximum fault level shall be calculated considering PSS-2 400 KV Bus as infinite Grid / Bus |
|  | Metallic screen ground fault current capability for 1 sec | kA | Maximum fault level shall be calculated considering PSS-2 400 KV Bus as infinite Grid / Bus |
|  | Specific Requirements and Quantity |  |  |
|  | No of cores | - | As per system requirements |
|  | Quantity required. | km | As per project requirement |
|  | Cable Size | - | As per tender requirement |
|  | Drum length requirement | - | As per project requirement |

- Tests

Cables offered shall be type tested and proven type. Routine tests as per IEC/IS standard shall be carried out on 100% drums. Acceptance tests & Special Test shall be carried out on no. of drums selected on random basis in the lot as per IS 7098 Part-I (Appendix-A) & Part-II (Annexure-D), of each type and size of cable of each lot. Bidder / Cable manufacturer shall provide the Type Test & Special Test reports as per Cl. No. 12.2 of IEC-62067.

| 1 | Routine tests as per IEC /IS standard |  |  |
| --- | --- | --- | --- |
|  | - Electrical resistance of conductors | - | As per IEC 60228/ IS 7098-2 |
|  | - Partial Discharge test | - | As per IEC 60885-3/ IS 7098-2 |
|  | - Voltage test | - | As per IEC 60502-2/ IS 7098-2 |
|  | - Overall Diameter test | - | As per IEC 60502-2 / IS 7098- 2 |
|  | - Tan δ measurement for cables |  | As per IEC 60502-2:2014 |
| 2 | Sample tests | - | As per IEC 60502-2 / IS 7098- 2 |
| 3 | Type tests, Electrical |  |  |
|  | - Bending test | - | As per IEC 60502-2 / IS 7098-2 / IS 10810 |
|  | - Partial Discharge test | - | As per IEC 60885-3/ IS 7098-2 |
|  | - Tan δ measurement for cables | - | As per IEC 60502-2:2014 |
|  | - Heat cycle test | - | As per IEC 60502-2 / IS 7098-2 / IS 10810 |
|  | - Impulse test followed by a voltage test | - | As per IEC 60502-2:2014 |
|  | - Voltage test for 4 h | - | As per IEC 60502-2:2014 |
|  | - Impulse test | - | As per IEC 60502-2 / IS 7098- 2 / IS 10810 |
|  | - Insulation resistance measurement at maximum conductor temperature | - | As per IEC 60502-2/ IS 7098- 2 / IS 10810 |
| 4 | Type tests, Non-Electrical |  |  |
|  | - Measurement of thickness of insulation | - | As per IEC 60811-1-1 / IS 7098- 2 / IS 10810 |
|  | - Measurement of thickness of non-metallic sheaths | - | As per IEC 60811-1-1 / IS 7098- 2 / IS 10810 |
|  | - Tests for determining the mechanical properties of insulation before and after ageing | - | As per IEC 60811-1-2 / IS 7098- 2 / IS 10810 |
|  | - Tests for determining the mechanical properties of non-metallic sheaths before and after ageing | - | As per IEC 60811-1-1 / IS 7098- 2 / IS 10810 |
|  | - Additional ageing test on pieces of completed cables | - | As per IEC 60811-1-2/ IS 7098- 2 / IS 10810 |
|  | - Loss of mass test on PVC sheaths of type ST2 | - | As per IEC 60811-3-2 / IS 7098- 2/ IS 10810 |
|  | - Pressure test at high temperature on insulations and non-metallic sheaths | - | As per IEC 60811-3-1 / IS 7098- 2 / IS 10810 |
|  | - Test on PVC insulation and sheaths at low temperatures | - | As per IEC 60811-1-4/ IS 7098- 2 / IS 10810 |
|  | - Test for resistance of PVC insulation and sheaths to cracking (heat shock test) | - | As per IEC 60811-3-1 / IS 7098- 2 |
|  | - Water absorption test on insulation | - | As per IEC 60811-1-3 / IS 7098- 2 |
|  | - Shrinkage test for XLPE insulation | - | As per IEC 60811-1-3 / IS 7098- 2 |
|  | - Thermal stability test for PVC insulation | - | As per IEC 60811-3-2 / IS 7098- 2 |
|  | - Flame spread test on single cables | - | IEC 60332-1-2 / IS 7098- 2 |
|  | - Shrinkage test for PE over sheaths | - | As per IEC 60811-1-3 / IS 7098- 2 |
| 5 | Special Tests |  |  |
|  | - Oxygen index test | - | IS 10810 Part-58 |
|  | - Temperature index test | - | IS 10810 Part-64 |
|  | - Acid gas generation test | - | IS 10810 Part-59 |
|  | - Smoke generation test | - | IS 10810 Part-63 |
|  | - Flammability tests | - | IS 10810 Parts-53 and 62 |
|  | - Flame retardant test | - | IS 10810 Part-61 |
| 6 | Acceptance, Routine and Type Test for HDPE outer sheath (ST-7) cable | - | IEC 60811/ IS 7098-2 |

|  | Data to be furnished by vendor after award of contract - Drawings / Documents for Approval: - Completely filled-in Data Sheets and Schedules. - Technical particulars of cable cross sectional drawing, QA Plan and technical catalogues. - Estimated weight of cables and cable drums. - Experience list where cables of similar rating and sizes have been installed and are in satisfactory operation. - Type test certificates/reports for the equipment covered in the specification. - Any other drawings/documents considered necessary - MQAP & Field quality plan as per CEA regulations - Cable sizing calculation |
| --- | --- |
|  | - Drawings / Documents for information: - Continuous current rating of the cable - General technical data - Construction details including type of material used and thickness of each material for each type of cable in a tabular form. - Instruction Manuals - Type/Routine test certificates for all types of cables included in the order and special tests on cables in line with applicable standard. - All detailed catalogues and literature of Cables supplied. - Any other drawings/documents considered necessary |

## B9 – SCADA SYSTEM

|  | SCADA |
| --- | --- |
|  | - This Section specifies the minimum requirements for design, engineering, installation, and testing of the PV Plant Scada System. Bidder to note that for each 1x300 and 1x200 MW (AC) block one dedicated SCADA system is required. The SCADA system shall be placed in “PV Plant SCADA, Monitoring and Spare room” building. OR Bidder may utilize space in PSS-2 for installation of SCADA system. Space for 6nos. of SCADA Panel is available in Server Room of PSS-2 and space for 6 nos. Workstation is available in Control room and SAS room of PSS-2. The Workstation console/furniture and Chair shall match with console/furniture and Chair of Control room and SAS room of PSS-2 for aesthetic view. The Workstation Monitor supplied for SCADA system shall match with the monitor of PSS-2. For installation of Workstation and Panel, all required materials and works (Civil and Electrical) shall be in scope of bidder. The SCADA includes all the software, hardware, wiring, servers, infrastructures, Gateway, Networking Equipment, HMI, Laser Printer etc., required to provide the monitoring, control and management capabilities described in this section. The provided system shall include a Graphical User Interface (GUI) for display and representation of data. The Scada must be permanently connected to the internet and the software platform shall have the ability to be accessed remotely and locally with an HMI machine. The Scada hardware infrastructures shall be in the Control Room along with all required supporting equipment. Communication equipment installed shall be interoperable, to allow seamless integration between different vendors. - The SCADA system shall be designed with Redundant and HOT stand by. - All 33KV switchgears, IEDs, Meters, ABT meters (SEM), all other electrical equipment like, Battery charger, UPS, NIFPS etc. shall be fully integrated to SCADA system in comprehensive manner for monitoring and control with time synchronization. - Reliability of SCADA shall be as per CEA Technical Standards for Communication System in Power System Operations 2020 and amendments. |
|  | - The system must be designed, engineered, and installed for Solar Project by an experienced integrator/provider with proven track record of successful installations with WRLDC as per latest guidelines of CEA/Verbal or written instructions of WRLDC. All component manufacturers must be ISO 9001 certified. All software must be modular and be programmed using open-source programming languages. - All software License shall be perpetual/ SCADA life. - In case of anti-virus software, the license shall include regular updates until the end of warranty and three (03) year’s annual maintenance contract (AMC) period. - Any defect in the software, which may arise during defect liability period and AMC period of the system shall be fixed at no cost to the Owner. During warranty period for any fault in entire SCADA package, the fault shall be rectified within 24 hours from time of intimation given to bidder/O.E.M and system should function with all functionalities as at time of commissioning. - All software with license and key shall be handed over to GIPCL. |
|  | Control and monitoring of photovoltaic systems and Inverters is essential for reliable functioning and maximum yield of PV solar electric system |
|  | A common, centralized, Supervisory Control and Data Acquisition System (SCADA) is envisaged for providing control and monitoring functions related to PV solar plant, Electrical system shall be envisaged |
|  | The PLC based Scada System shall monitor, control and process alarms of all required components and be able to integrate and display information of such components in a single software platform. The Scada must accumulate functions of control, monitoring, data processing and analytics and supervision and alarm management. |
|  | The Scada should be designed and engineered with the following guidelines: - The system should have high availability, stability, and reliability as per CEA Technical Standards for Communication System in Power System Operations 2020 and amendments during its operations and usage. - The solution should allow scalability to include the possibility of expansion of the system without rearrangement of the existing system architecture, allowing an increment just by adding equipment. - Architecture should be simple and should be modular to account for system maintenance, addition and correction of features or components to the system |
|  | I&C system shall permit centralized operation of the plant from the Main Control Room in the control building. The Human Machine Interface (HMI) of the SCADA shall be housed in the Main control room in the control building |
|  | The Plant SCADA (Supervisory Control and Data Acquisition) software applications consists of acquisition and gathering of all information generated by the solar plant equipment such as fiscal meters, inverters, recombiner box, network analyzer, weather stations, data loggers and trackers. |
|  | The SCADA is composed for software and hardware, and it is designed for local and remote monitoring, historical trending, and operation of the plant. Receive in real-time plant information for all plant monitoring. |
|  | All services including specialized services necessary for proper erection, testing and commissioning of all items of the package covered under this proposal shall be arranged by the Bidder. The SCADA shall be of latest OPC version 2.05a or higher compliant and implement an OPC- DA 2.05a server as per the specification of OPC Foundation |
|  | SCADA system shall support Modbus (TCP/IP, RS-485), RTU, ASCII, IEC 61850, IEC 60870-5-101 & 104, FTPs, Licensed Web based secured remote monitoring (for 4 simultaneous users), standard protocols (Included but not limited to) to communicate with different sub system/Devices. Web based secured remote monitoring shall work on popular web browser without need of additional software. It shall be authorized by user ID and password. User Id and password for remote view can only be changed by SCADA administrator. Internet connection for transferring data to web shall be taken by Bidder in name of GIPCL site for O&M period. |
|  | Web access through a VPN client server firewall (minimum bandwidth recommended: 1Mb/s for Upload and 1Mb/s for download) for secure transmission over IP networks |
|  | SCADA shall provide for the following control / monitoring as per CEA Technical standards and amendments - PV plant Monitoring– Zone monitoring at Inverter Level in case of Central inverter - In case of String inverter - monitoring at recombiner box level - Control and monitoring of Plant electrical equipment, Feeders and their energy meters (Tariff based / Performance based) etc. - Provision for remote Enterprise system interface for MIS - PPC (power plant Controller) redundant PPC shall be provided at PSS -2 for 500 MW. - Tracker System - Module Cleaning System dry and wet (if applicable) - UPS and battery chargers - NIFPS - Fire Protection System - Weather Station |
|  | SCADA shall have the following hardwired / Soft links to facilitate the below: - Weather station data (Soft link) - Soiling Station - Inverter parameters, alarms, and ON/OFF Command (Soft link) - Transformer monitoring (hardwired) - HT Switchgear all equipment including annunciator - NIFPS Integration with SCADA - UPS and Battery Charger data (Soft Link) - Display and storage of derived/ calculated/ integrated values - Tele protection, Data and Speech communication with WRLDC/KPS-II as per CEA technical standards and regulation and amendments |
|  | 5% spare IO shall be considered for engineering contingencies and 10% overall spare shall be considered for each type of module for future expansion. |
|  | Critical plant and Outgoing Feeder related parameters shall be made available online and shall also be historized, for offline analysis to track plant performance and ensure asset availability. SCADA shall provide 1, 15, 30 minutes interval daily, monthly, and annual average of all the measurements. PPC reports shall have minimum 1 sec time resolution or as per CEA requirements. All reports shall be made available in CSV, MS Excel file type. It also generates, store and retrieve user configurable periodic report. |
|  | Provision for Licensed Web based secured remote monitoring shall be provided at least for 4 simultaneous users. |
|  | All systems shall be “State of the Art”, (Latest Technology) with a proven track record, suitable for the entire range of site ambient conditions as specified in Specification. |
|  | Entire equipment pertains to the I&C system including SCADA system shall not get obsolete within 15 years of taking over of the complete plant. The bidder shall provide spares and service support letter on O.E.M letter head for the offered systems for at least 15 years from COD. |
| - 1 - 1 - 1 - 1 | Bidder shall ensure appealing aesthetics and ergonomic designs while selecting control room consoles, HMI equipment and furniture and obtain Owner’s prior approval for the same. The SCADA system from Solar Power Plant to PSS-2 Common communication Panel shall be connected through 2 nos. of Optical Fiber Cable (armored). - First optical fiber shall be used for IEC 104, VOIP, OPC, Power Tel broadband connectivity. - Second optical fiber shall be used for IEC 104, VOIP, OPC. For more details bidder shall refer to PSS-2 DWG NO FCE-171125-CI-DWG-CMS-4100-002. The control system shall provide safe operation under all plant disturbances and on component failure so that under no condition the safety of plant, personnel or equipment is affected. Control system shall be designed to prevent abnormal swings due to loss of Control System power supply, failure of any Control System component, open circuit/short circuit. On any of these failures the controlled equipment/parameter shall either remain in last position before failure or shall come to fully open/close or on/off state as required for the safety of plant/personnel/equipment and as finalized during detailed engineering. System shall be designed such that there will be no upset when power is restored. This operation shall be demonstrated by vendor during Factory Accepted Test (FAT) in the presence of GIPCL Representative. Power plant controller (PPC) shall be provided with two processors (main processing unit and memories), one for normal operation and one as hot standby. In case of failure of working PPC processor, there shall be an appropriate alarm and simultaneously the hot standby PPC processor shall take over the plant control function automatically. The transfer from main processor to standby processor shall be totally bump less and shall not cause any plant disturbance whatsoever. It shall be possible to keep any of the PPC processors as master and other as standby. The standby processor shall be updated in line with the changes made in working processor. The solar plant SCADA and PPC networks shall be suitably designed, so that PPC shall directly and independently able to control the individual solar inverter. Detailed control logic in the PPC shall be finalized during detailed engineering stage. |
|  | The cyber security program shall address the following (to be complied for 500 MW): - Compliance with provisions of the Information Technology Act, 2000 (21 of 2000) and National Cyber Security Policy, 2013 as amended from time to time. - Implementation of the National Critical Information Infrastructure Protection Centre (NCIIPC) Guidelines. - Implementation of guidelines and advisories issued by Computer Emergency Response Team (CERT India) and applicable Sectoral Computer Emergency Response Team (CERT). - Compliance to the Central Electricity Authority (Cyber Security in Power Sector) Guidelines 2021 and amendments - The bidder shall conduct cyber security audit of their entire SCADA Infrastructure after commissioning of SCADA through CERT-In empanelled Auditors so as to identify gaps and appropriate corrective actions shall be taken by bidder. - In audit Vulnerability Assessment of SCADA infrastructure shall be carried out. If SCADA is found vulnerable to any exploits or upon any patch updates or major configuration changes, then further Penetration Testing may be carried out offline or in a suitably configured laboratory testbed to determine other vulnerabilities that may have not been identified so far. - Bidder shall submit the audited report and comply with the requirement if found any in audit report within the time frame as required/mentioned by GIPCL, without any additional cost to GIPCL. |
|  | CODES AND STANDARD |
|  | The following Indian Standard Codes, unless otherwise specified herein, shall be applicable. In all cases, the latest revision of the codes shall be referred to: |

|  | Codes | Description |
| --- | --- | --- |
|  | IEEE | The Institute of Electrical and Electronic Engineers |
|  | ANSI | American National Standards Institute |
|  | IEC | International Electrochemical Commission |
|  | EN | European standards |
|  | ITU | International Telecommunication Union |
|  | ISO | International Standards Organization. |
|  | ISA | Instrumentation, Systems and Automation society |

|  | ### DESIGN CRITERIA |
| --- | --- |
|  | DATA ACQUSITION, STORAGE AND ANALYSIS |
|  | The SCADA shall acquire process and analyses data. All required components shall have communication protocols compatible with the SCADA and all communication lines and infrastructures shall be included in the monitoring system. After acquisition of data the software platform shall be capable of providing the following analytics and reporting: - Yield and Performance Ratio (PR) calculation. - Display of reports, events, and alarms. - Creation and scheduling of reports of PV plant KPIs trends for different time scales, such as hourly, daily, monthly, and yearly. - Display of overall plant layout, individual equipment status and areas with colour codes for each area of the PV Power Plant in the GUI. - Max irradiation, annual irradiation and generation today, month and year with date. - Block number and 15 min generation in that block / as per the regulation requirements. - Any other requirement as required by GIPCL. - All data acquired during the lifespan of the plant must be logged, archived and available in the platform. |
|  | The acquired data shall be stored in local servers and periodically send to Historian. Acquisition system parameters: - Monitoring stations, SCADA Hardware, Accessories and Communication Link - Weather station - Inverter - Alarms and warnings of PV equipment - Main PV Plant Switch - Monitoring of electrical parameters of Energy Meter, SEM (ABT), Disturbance Recorders, MFM, PQ Meter, Numerical relay , All IEDs, Fire alarm panel, GPS, Transformers, Trackers - Data logger equipment - Reading of network analyzers - Supervisor of systems and protections (team that monitors the status of the protection low voltage and medium voltage). - HT Switchgear equipment - UPS and Battery Charger (if required) parameters - Any other equipment parameters required |
|  | The connection between different field communication devices (Inverters, network analyzers, weather station, etc.) and the server will be made through the local network installation, using switches to group equipment. The field communication devices will be located on the control box at each power station. Through the fiber optic (Single mode) the data collected from the power stations, meter and weather stations will be carried to Main switch panel into the Main Control box located at control room. |
|  | The Scada shall have control functions to issue commands and settings to the control enabled equipment. Control functions of the PV power plant shall include at least: - Remote and local curtailment of power, through issuance of commands to the PV inverters as per requirements of local grid codes and regulations - Control functions shall allow a reaction time for ramp up and ramp down of PV output power at a rate in compliance with local grid codes and regulations - Reaction time for controls and curtailment of PV inverters shall the shortest possible and must comply with local grid codes - All limits and thresholds shall be easily adjustable remotely and via local operator login at the HMI - Remote control (on/off) of PV inverters, main switchgear including setting of all parameters - Other required control functions not listed in this document required by local grid codes and regulations. |
|  | Following Meteorological Station data shall be included in SCADA For each of the installed meteorological stations: - Ambient temperature, in ºC - Back of module cell temperature, in ºC - Global Horizontal Irradiance from pyranometer, in W/m2 - Global irradiance in collector plane from a pyranometer, in W/m2 - Diffused irradiance from pyranometer, in W/m2 - Wind speed, in m/s. - Wind direction, in degrees - Cloud in % - Rain falls in mm - Humidity - Weather station communication status |
|  | Following INVERTER minimum data shall be included in SCADA - Inverter alarms including diagnostic alarm - DC voltage, in V DC - DC current from each input, in A - Power supply voltage, in V - Power supply load, in kW - AC output apparent power, in kVA - AC output active power, kW - AC reactive power, kVAr - Power Factor - Phase angle, in degrees - For each output AC phase - Voltage, in V - Current, in A - Active power, in kW - Reactive power, in kVAr - Apparent power, in kVA - Temperature inside the inverter - AC switch position (open or closed) - AC trip status - All other standard PV inverter parameters - Communication status - ON/OFF command to Inverter - Disturbance recorder - Any other parameters as required by GIPCL |
|  | Following Energy Meters minimum data shall be included in SCADA - Active (kWh) and reactive (kVArh) exported energy at the output of the inverter. - Active (kWh) and reactive (kVArh) imported energy at the output of the inverter. - Frequency (in Hertz) at the output of the inverter. - Harmonics - True RMS of current (in Amperes), voltage (in Volts) and power (in kW): average, actual, maximum, and minimum, for each of the phases of the output of the PV inverter. - Voltage shall be measured at the middle of each pair of cables in the inverter output bus. - Current shall be measured by high accuracy current transformers and the point of measuring should be in the output cables of the inverter. - Communication status - Any other parameters as required by GIPCL |
|  | Following MV Switchgear minimum data shall be included in SCADA - MV 33 KV Breakers sttauts – On, OFF, Trip, Spring charging status, Service , Test, Local, remote, etc. . - Status of transformer MV switch for pressure, temperatures, Buchloyz, etc. - Communication status - Any other parameters as required by GIPCL |
|  | Following Plant Delivery Station minimum data shall be included in SCADA - Switching station temperature. - Status of each switch for each loop line, transformer and exit line (open or closed). - Transformer trip status from pressure and/or pressure. - Status of protection from the current transformer cell and its protection fuses (blown or ok). - Status of each protection relay. - Differential pressure and its status. - Status of cooling fans. - Communication status of all devices in the room. - Any other parameters as required by GIPCL. |
|  | Following Fire Protection Devices minimum data shall be included in SCADA - Alarm status of MV switching cell room. - Alarm status of Plant Delivery Station. - Alarm status of buildings. - Any other parameters as required by GIPCL |
|  | HARDWARE & SOFTWARE REQUIREMENTS |
|  | PV Plant SCADA, Monitoring and spare room building shall have the following feature: - Facility for implementation of all logic functions for control, protection and annunciation of the equipment and systems. - SCADA shall be provided with two processors (main processing unit and memories), one for normal operation and one as hot standby. In case of failure of working processor, there shall be an appropriate alarm and simultaneously the hot standby processor shall take over the complete plant operation automatically. - The transfer from main processor to standby processor shall be totally bump less and shall not cause any plant disturbance whatsoever. - In the event of both processors failing, the system shall revert to fail safe mode. - It shall be possible to keep any of the processors as master and other as standby. The standby processor shall be updated in line with the changes made in working processor. - The memory shall be field expandable. - The memory capacity shall be sufficient for the complete system operation and have a capability for at least 20% expansion in future. - Programmed operating sequences and criteria shall be stored in non-volatile semiconductor memories like EPROM. - All dynamic memories shall be provided with buffer battery backup for at least 360 hours. The batteries shall be lithium or Ni-Cd type. - A forcing facility shall be provided for changing the states of inputs and outputs, timers, and flags to facilitate fault finding and other testing requirements. It shall be possible to display the signal flow during operation of the program. - Bidder must provide suitable hardware DMZ network firewall to restrict unauthorized access to HMI/ SCADA system. |
|  | State of the art microprocessor-based SCADA system for Plant control and monitoring including PV solar plant, BOP systems, Electrical system. In addition, SCADA shall facilitate optimized inverter control. The performance, memory and hard disk of the workstation shall be sufficient to fulfil the requirements specified in this document and supports its activities throughout the lifetime of the plant. Also, one number mini-PLC controller shall be mounted in each Inverter Room. |
|  | Human Machine Interface (HMI). |
|  | One number CCTV workstation, One number PPC workstation, Two number Tracker Workstation, One number Robotic Workstation, Two numbers Operator workstation, One Engineering workstation, one redundant historian server, one OPC Server, one laptop with EWS and OWS programming and two gateway systems (one is main and Redundant) with LED monitor.All monitor shall be 42” size, except CCTV monitor which shall be 50” size. Both the systems to be connected to redundant servers (24x7). The Systems to be functionally interchangeable. I.e., The function of both Engineering station and operator station shall be possible from both the systems. Operator shall be able to access all control/information related data under all operating conditions including a single processor and computer failure/hardware failure. Bidder shall provide dedicated Laptop configured to work as Operator cum Engineering Workstation. |
|  | All the required software to be provided including supply of Graphic interface card for implementation of control logic, operator station displays / logs, storage & retrieval and other functional requirement shall be provided. The programs shall include high level languages as far as possible. The Bidder shall provide sufficient documentation and program listing so that it is possible for the GIPCL to carry out modification later. |
|  | The SCADA shall include two (2) redundant Control Unit Servers working in hot-standby mode. The performance, memory and hard disk of Control Unit servers shall be sufficient to fulfil the requirements specified in this document Hard disk for archiving shall be a RAID05 system providing resilience against a single hard disk failure. The servers shall have the high reliability, easy maintenance and shall be of 19” industry standard rack-layout design with slide-out rails, collapsible, high resolution. As a minimum, the servers shall meet at least the following: - Redundant monitored power supply, hot pluggable - Monitored cooling fans - Redundant hot pluggable, hot swappable hard disk array - Power supply: redundant from UPS |
|  | One number A4 colour Laser printer equipped for colour laser printing, scanning, copying and faxing facility. |
|  | Redundant Server based Network Panels including Network switches, Remote wireless connection related interface devices etc. |
|  | The Bidder shall provide standard hardware and software configurations to the extent possible if it meets or exceeds the requirements of this Specification. International standards shall be applied for hardware and software interfaces to allow system expansion in terms of equipment and software functions (if required). |
|  | Licensed software copy required for the proposed system shall be provided. The latest proven antivirus software shall be installed in the SCADA |
|  | All logins to the system shall be password protected. Data transmission via public internet shall be encrypted. |
|  | Application software, MIS software & HMI software to meet the specified functional requirements of SCADA. |
|  | Sequence of Events recording and annunciation system – integral to SCADA system. |
|  | Historization and archiving relevant data for analysis. |
|  | Interposing relays, isolators as required. |
|  | Control desk, Control panel, system / marshalling cabinets, as required. |
|  | All Instrumentation & Control cables, serial link cables, single mode / Multi mode armored fiber optic cables, SCADA system cables etc., between any two-system supplied by Bidder. |
|  | 2x100% Redundant 230VAC UPS for SCADA, mini-PLC in PVCS. UPS shall be provided as per CEA requirement. Or 2 hours backup from each battery bank whichever is higher. |
|  | Required Power Distribution Boards as required for distributing the UPS / other power supplies to all consumers of the total system. |
|  | MIS Server for Enterprise network interface. |
|  | Dedicated Earthing system (separate electronic and frame earth). |
|  | Emergency local push buttons. |
|  | Control panel to be in Control room, with operating, monitoring hardware and Annunciation system as per system requirement. |
|  | GPS Master clock-They shall be connected, and time synchronized via the Global Positioning System (GPS). All measured data, events, alarms, logs etc. shall be time stamped with a 1msec resolution. A master clock (e.g., via GPS) shall be provided and shall be used for time synchronization of all auxiliary systems and equipment of the PV power plant such as Meteorological Measurement Station, etc. |
|  | The Scada shall be based on standard proven firmware and software, which shall already be implemented in other systems. The software engineering tool shall be provided to configure, set up and modify the data acquisition, data processing and database system components. The software application shall include facilities to perform programmable logic functions. |
|  | The system shall have monitoring and self-diagnostics features for both, hardware, and software. Licensed software copy required for the proposed system shall be provided. The latest proven antivirus software shall be installed in the SCADA. All logins to the system shall be password protected. Data transmission via public internet shall be encrypted. Application software, MIS software & HMI software to meet the specified functional requirements of SCADA. Sequence of Events recording and annunciation system – integral to SCADA system. Historization and archiving relevant data for analysis. The Bidder shall provide software license for all software being used SCADA system. The software license shall be provided for the project (e.g., Organization or Site License) and shall not be hardware/machine specific. That is, if any hardware/machine is upgraded or changed, the same license shall hold good, and it shall not be necessary for GIPCL to seek a new license/renew license due to up gradation/change of hardware/machine in SCADA system at Site. All licenses shall be valid for the continuous service life of the plant. All SCADA software with license shall be handed over to GIPCL. All hardware and software shall be licensed to GIPCL. |
|  | PARAMETRIC REQUIREMENTS The control system shall be designed such that under worst case loading conditions the response time shall not be worse than the following: - - On/Off Command: - The response time for screen update after the execution of the control command from the time the command is issued shall be one second (excluding the drive actuation time). - Adjustment Command: - 0.5 to 1 second. - On screen Updating and All Control related displays: - 1 second. - Bar Chart displays, Plant Mimic displays, Group review displays, X-T Plot Displays and Plant Summary Displays: - 1 to 2 seconds. All the Analog data shall be scanned at the resolution of 1(one) second and refreshed on screen however, recording of data shall be as finalized during detail engineering. |
|  | PLANT PERFORMANCE CALCULATION & TRACKING IN SCADA SYSTEM |
|  | SCADA shall have provision to calculate and display the following: - Performance Ratio. - Energy yield - Day, month, annual generation curves etc. - Displays shall also include current and histories trends for generation curve, yield curve, module temperature variations, wind velocity, radiation variation etc., - Individual Inverter performance shall be tracked and displayed. |
|  | ARCHIVING SERVER SYSTEM |
|  | Multiple, dedicated RAID disk systems shall be provided in all servers, to maximize system throughput and minimize data exchange delays. |
|  | Disk drives that make up the RAID array shall be hot pluggable and be capable of being replaced online. The system shall be capable of automatic recovery from a single disk drive failure. |
|  | Each disk array’s total capacity shall be expandable in configuration and adding more drives, with no requirement to physically shutdown of the disk array and restart the system. |
|  | Minimum capacity of the data disk array that is useable data storage shall be 1TB and shall be of sufficient qty to store data for duration of three (3) years. |
|  | For regular backup of the RAID data storage array a Network Attached Storage unit (NAS) shall be provided. The unit shall have a sufficient capacity to allow: - Complete backup of the whole server and workstation operating system files and application programs – this backup to be done by the system administrator on monthly basis. Only one historical backup and one actual backup shall be maintained on the storage unit. - The unit shall be capable to ensure backup capacity of those files for a continuous period of 6 months. An alarm shall be raised when the NAS capacity decreases to less than 20%. |
|  | Equipment for automatic backup of operator workstation and Central Unit Servers shall be provided. Removable media (e.g., hard disk, DVD or similar) shall be provided to enable storage of backups |
|  | INVERTER TRIP ANALYSIS Inverter trip mechanism and settings shall be tuned site specific to match with the evacuation system requirements. Inverter trips and causes of trips shall be logged with a sequence of events recording feature of SCADA with millisecond resolution. |
|  | HISTORIZATION AND ARCHIVING - Data temporarily stored in inverters memory shall be periodically acquired in PLC hard disk. Data logging shall be envisaged for various environmental and PV plant system related parameters and shall facilitate detailed overview about the whole system. User configurable trend and Report formats shall be available. - Alarm, Event, Periodic plant data, selected logs/reports History shall be available for archiving. - The Historian shall collect, store and process system data from SCADA data base. The data shall be saved online on hard disk and automatically transferred to nonerasable long term storage media once in every 30 Days periodically for long term storage. Provision shall be made to notify the operator when hard disk is certain percentage full. - The system shall provide user-friendly operator functions to retrieve the data from historical storage. It shall be possible to retrieve the selected data on operator cum engineering workstation in form of trend/report by specifying date, time & period. Further, suitable index files/directories shall also be provided to facilitate the same. - In addition to above, the system shall also have facility to store & retrieve important plant data for a very long duration on portable external long term storage media. Bidder shall provide two numbers of portable external hard drive of 2TB each. - For long term plant performance analysis, the following plant data as a minimum with time stamping and interval as indicated in below table but not limited to shall be stored daily on historian. - Important plant data for a very long duration (plant life) Storage on Historian Sl.; Parameter; Time Interval *. 1; Weather Monitoring Stations data: Global Horizontal Irradiance, Global Inclined Irradiance and Diffuse Horizontal Irradiance, Ambient Temp, PV Module Temperature, Wind Speed, Wind Direction, Rain Fall and Relative Humidity.; 1 (One) Minute. 2; Calculated Daily Global Horizontal Insolation, Global Inclined Insolation and Diffuse Horizontal Insolation.; 24 (Twenty-Four) Hours. 3; Inverters: DC Voltage, DC Power, DC Current, SMB/SMU Current (Inverter end), AC Active & Reactive Power, Power factor, AC Current & Voltage, Energy, Inverter room temp, Inverter Cabinet temp and Modules Temp; 1 (One) Minute. 4; MFM, Energy meter and Numerical Relay data: - Active & Reactive Power, Energy (day), Current and Voltage; 1 (One) Minute. 5; Export feeder/s Energy Meter Data: - Active & Reactive Power, Energy import and export, Current and Voltage and Grid Frequency; 1 (One) Minute. 6; Daily energy export from each Inverter; 24 (Twenty-Four) Hours. 7; Total sum of daily energy export from all Inverter; 24 (Twenty-Four) Hours. 8; Disturbance recorder (IBR); For each event. * The time interval shall be in compliance with relevant CEA regulation / RLDC requirement etc. |
|  | OVERALL SCADA PERFORMANCE REQUIREMENTS - All equipment shall be of high quality and reliability. The overall system availability of the shall be 99% or better. - Loss of monitoring data shall be avoided by means of redundant hard disk drives or RAIDs and an appropriate automatically operating backup technology for removable media. - The SCADA Manufacturer shall provide service support for minimum 15 years. - Diagnose performance issues (soiling, incorrect alignment) detection and alarms Optimize solar farm operations and maintenance (panel cleaning schedule) - Track Module performance, weather monitoring system data, irradiance - Evaluate long-term system reliability and performance, inverter failure rate etc. - Track System Losses to provide basis for upgrades - Online “Overall Photovoltaic System Performance Monitoring” as per IEC 61724 - Alarm detection and management and alerts to minimize the equipment downtime. - Integrated Reporting system to meet compliance requirements - Online Weather-corrected PR calculations for mapping consistent results throughout the year, as a metric for performance guarantees & for use in predicting actual annual system yield - Remote connection to Module, Inverter OEM Centers for remote diagnostics and immediate corrective actions (Optional) - Online calculation and reporting of carbon credits under CDM. |
|  | SCADA GRAPHICAL USER INTERFACE (GUI) REQUIREMENTS - HMI configured around latest state-of-the art servers/Workstations with open architecture supporting OPC /TCP/IP protocols, etc. - Display of status of major equipment in Single Line/Mimic Diagram. Mimic Diagram colour shall comply to IS 11954: Guide for colour coding of electrical mimic diagrams. |
|  | Screen shots shall cover topography of the layout with dynamic colour change based on generation Daily plant PR, plant down time and the cumulative inverter down time shall be displayed on the main screen. |
|  | Clear indication of screen for Summary, IR, Block, SLD DC, SLD AC, SLD Communication Architecture, Customized and defined Report, Data Flow to SLDC, String / SMB, Tracker, Alarm, Trend to choose and drop any parameter for comparison graphically. |
|  | Operation of plant along with central restriction for load to be injected. |
|  | From the main screen plant layout, one should be able to enter any specific block by pressing on that block in the plant layout Overview Screen |
|  | In the inverter summary page, the fault description shall be indicated. |
|  | All weather station data, meter data, relay data (numerical relay, protection relay etc.,) shall be displayed block wise. |
|  | Fault locations (E.g., Earth, LV/HT panels) shall be displayed. |
|  | On the Outgoing Feeder screen, the AC SLD should be displayed. All circuit breakers, positions should be displayed and controllable remotely (with layered security access) from this page. Another pop-up should allow navigation to details of the 33kv switchgear panels which should display (red/green) the mimic diagram, and all alarms and positions of switches. Transformers winding temperature & oil temperature should be displayed and logged. Grid failure indication and battery charger failure indication should have displayed here and the main screen as well. The mimic shall be configured on the HMI, and it shall be possible to control, monitor and operate the plant from the same. |
|  | All 33kv transformers winding temperatures & oil temperatures in each block should be displayed and logged. |
|  | SCADA access should be layered as per criticality and each layer should be password protected. |
|  | Remote access of the system should be layered, and password protected. |
|  | On the main screen, actual power of each inverter shall be monitored with the other inverters and if the difference is more than a set value (e.g., 10 kW), an indication / alarm should appear on the front screen for that inverter tag |
|  | The graphical display should allow plotting plant AC power, plant DC power, GHI, GTI, average irradiation of all pyranometers, and individual irradiation of all pyranometers, Module surface temperature & ambient temperature values. |
|  | There should be separate generation of all Event logs, Fault logs, inverter logs (including individual inverter down time), alarm logs, transformer winding and oil temperature logs. |
|  | All the above specified data shall be available in SCADA for the last 30 days. |
|  | Alarm signals shall be accompanied by hooter /Buzzer. |
|  | The SCADA shall have a view displaying a connection single line diagram with different voltage levels. The current state of all equipment/plant sectors shall be displayed using a colour code. |
|  | The equipment access structure should be organized in a logic hierarchy. When selecting equipment in the platform, a new view shall be shown with detailed information and the appropriate graphs or tables (power, currents, availability, etc.) about the device. |
|  | The main view shall be a plant map with different areas corresponding to each inverter. |
|  | Each different section of the plant named, and its status shall be distinguished by colour gradient from green to red, with full red being an error/alarm. When selecting a section, it shall trigger a detailed view of all information relating to that section. |
|  | The main view shall include a section of the screen dedicated to display information of total production and of also of each plant sector. |
|  | In other data directly from the plant we will have a record of historical data, alarms and events. These historical are represented by tables or diagrams. |
|  | The above data shall be available via the Web portal. |
|  | The operator workstation shall have minimum but not limited to the following interlinked display graphics: - PV Power Plant Overview with user adjusted real time data display. - PV Plant Single Line Diagrams representation with overview and details for different voltage levels for all main electrical equipment including presentation of real time data and status (open/closed switches). - System parameter setting and command issuance management with command log and settings change log; The system shall have built-in safety features that will allow/disallow certain functions and entry fields within a function to be under password control to protect against inadvertent and unauthorized use of these functions. Assignment of allowable functions and entry fields shall be based on user profile. The system security shall contain various user levels with specific rights as finalized by the GIPCL during detailed engineering. However, no. of user levels, no. of users in a level and rights for each level shall be changeable by the programmer (Administrator). - Alarm and event management system including alarm and event list. - SCADA architecture along with communication network status. - Diagnostic screen including overall system architecture and status. - User configurable and adjustable views. - Programming of the SCADA and Historian shall be user friendly with graphical user interface and shall not require knowledge of any specialized language. For example, Flow-chart or block logic representing the instruction graphically or Ladder Logic, etc. - The programming of SCADA (like development and modification of data base, mimics, logs / reports, Historian functionalities etc.) shall also be possible through user-friendly menus etc. - All programming functionalities shall be password protected to avoid unauthorized modification. |
|  | SCADA ACCURACY AND COMMANDS / FEEDBACKS |
|  | The overall system accuracy from signal input terminals to output presentation on display and printers for the least accurate input range and maximum scan rate shall not be worse than + / - 0.1% of full scale of the engineering process range + / - 1/2 LSB for 4 - 20 m A input. |
|  | Monitoring of UPS, DC system, Weather station shall be included |
|  | Control and monitoring of all plant electrical equipment from Plant control room mounted consoles shall include – all HT/LT breakers, etc., |
|  | Monitoring shall include surge protection device monitoring, Inverter, Transformers, Relays (numerical and microprocessor-based protection relays), ABT Meters, MFM Etc.. |
|  | Virus scanners, Malware scanners, firewalls etc., shall be envisaged to protect SCADA system |
|  | Control of Electrical Equipment (Hardwired) |
|  | Commands: - Two Remote Commands from SCADA system to HT SWGR- Start /Stop. - Individual interposing relays for the above two commands shall be provided and mounted in respective SWGR. SCADA digital output (24 V DC) shall drive these relays. |
|  | Feedbacks: - SCADA shall include minimum 6 numbers of feedbacks (potential free contacts) for the following: - Breaker - ON - Breaker - OFF - Lockout relay activated - Trip circuit healthy - Breaker available - Breaker in Local/Remote |
|  | ABT Meters and multifunction meter interface comprehensive data to SCADA |
|  | Protection relay interface to provide individual protection activated, deactivated signals with time stamping |
|  | Operator Interface Graphics shall include - Control displays - Online Performance calculations (Management information system) - Configurable trends, X-Y plots - SER (sequence of events recording) with time tags - Configurable logs /Reports etc., - AC/DC SLD - Electrical Mimics - SMJB status - Inverter displays - Description of system architecture offered for this project (plant network, control network etc.) - Alarm (alarm segregation, history collection) & Event management (including sequence event recording) and alerts to minimize equipment downtime - Graphic implementation philosophies (Colour code, display builder settings, symbol philosophy pop up behavior, Font behavior, logs, phase plate display of controller & other electrical systems etc.) - Logic implementation philosophies - Hardware & Software diagnostics - System redundancies in Power supply, communication, controller etc. - Trend display & configuration - Mimic display for plant and different systems - Disturbance recording - Remote access facility - Grid synchronization details |
|  | SOLAR PV PLANT PERFORMANCE TEST |
|  | Integrated site performance test of PV plant, using SCADA shall be envisaged. The test would include verifying AC/DC losses and calculation of Performance Ratio. |
|  | Solar Modules are free Supply to the Bidder. Hence the following shall be specifically confirmed. - Overall Plant performance shall be carried out as per relevant sections specified in this tender. |
|  | The PV Plant performance test will be completed if the following is satisfied: - The transmission of all signals as required by the Grid Code is established. - The facility operates in accordance with the set point values for: - Active power - Reactive power (maximum leading reactive power and maximum lagging reactive power) (those set values will be agreed by the parties and approved by the Testing Expert) |
|  | EARTHING Separate safety earthing for enclosure and electronic earthing for electronic modules with dedicated earth pits |
|  | CABINETS |
|  | Central Unit Servers and associated accessories shall be accommodated in dedicated equipment cabinets. |
|  | For indoor application, the cabinets shall be constructed as follows - Standard sized steel cabinets with external painting colour as per Client’s approval. - Certified for minimum IP31 protection class. - Power distribution box with main filter and main switch (separate 2-pole breakers for each device). - Front-patches for LAN cabling. - Cable organizers, cable trays, suspensions, and termination components with strain relief for all internal and external cabling. - Overvoltage protection for all devices (if applicable). - Housing space for future equipment. - Ventilation fan to ensure proper equipment working temperature. - Bottom cable access. - Document pocket. - Grounding bus bar for grounding connections. - Doors with glass front and locking system. - Inner light and power socket for maintenance. - Provision of easy access for maintenance and repair, all devices with rear plugs shall be under a drawer type rack. |
|  | ALARM AND EVENT MANAGEMENT |
|  | All alarms including system alarms and important events shall be listed up on the display. The lists shall be in chronological sequence showing: - Time stamped, the precise date and time with the specified resolution in actual sequential of events shall be shown. - Clear identification of device alarm with clear text/denomination of alarms and/or events and status message (open, close, off, high, low). For the case of analogue values, the values shall be shown along with the thresholds. - Sorting of alarms per subgroup shall be possible. |
|  | Flashing functions of alarm messages shall be according to standards related to conventional alarm. The flashing frequency for coming and going alarms shall be adjustable. Alarms shall be checked to be cleared. |
|  | Automatic and configurable generation of typical reports with user selected variables shall be supported. It shall be possible to print the generated reports and export to common file formats. The format of the logs and reports shall be subject to the approval of the Client. |
|  | COMMUNICATION NETWORK INFRASTRUCTURES DATA COMMUNICATION SYSTEM The Data Communication System shall include a redundant Main System Bus with hot back-up. Other applicable bus systems like cubicle bus, local bus, I/O bus etc shall be redundant except for backplane buses which can be non-redundant. |
|  | The following are minimum features: - Redundant communication controllers shall be provided to handle the communication between I/O Modules (including remote I/O) and PLCs and between PLCs and operator workstation. - The design shall be such as to minimize interruption of signals. It shall ensure that a single failure anywhere in the media shall cause no more than a single message to be disrupted and that message shall automatically be retransmitted. Any failure or physical removal of any station/module connected to the system bus shall not result in loss of any communication function to and from any other station/module. - If the system bus requires a master bus controller philosophy, it shall employ redundant master bus controller with automatic switchover facility. - Built-in diagnostics shall be provided for easy fault detection. Communication error detection and correction facility (ECC) shall be provided at all levels of communication. Failure of one bus and changeover to the standby system bus shall be automatic and completely bump less and the same shall be suitably alarmed/logged. - The design and installation of the system bus shall take care of the environmental conditions as applicable. - Data transmitting speed shall be sufficient to meet the responses of the system in terms of displays, control etc. plus 25% spare capacity shall be available for future expansion - Cat 6 UTP or fiber optic cables shall be employed. - The Bidder shall furnish details regarding the communication system like communication protocol, bus utilization calculations etc. - Bidder shall setup Gigabit Ethernet based Plant Local Area Network (LAN) to connect to different communication nodes at Inverter /Switchgear location etc. with redundant backbone using ring or better topology. - For plant capacity more than 100MW (AC), there shall be more than one ring for each 100MW or part connecting field node (controller/switches) and CMCS SCADA in manner that there are equal nodes in each ring as for as possible. Each Modbus cable shall be provided with Surge protection device at SCADA Panel End. Specification of OFC and Modbus cable has been given elsewhere in this specification. |
|  | The network infrastructures of the SCADA, includes all hardware, wiring, connections, and equipment required to comply with the specifications defined herein. These components and hardware include, but not limited to cables, accessories, converters, repeaters, amplifiers, switches and routers, servers, UPS, equipment including accessories, their housing as required, as well as the management systems necessary to operate the data communication network. |
|  | The network design must include redundancy and account for reliability and availability as a design factor. All Ethernet infrastructures shall have a minimum data rate of 100 Mbit/s. |
|  | Uninterrupted power supply for the SCADA shall be provided by a UPS. All servers and data archiving servers shall have redundant power supply modules. |
|  | The Bidder shall perform all cabling and installation works for outdoor and indoor equipment as well as the interface interconnection and termination at existing devices. |
|  | INDUSTRIAL ETHERNET SWITCHES (MANAGED TYPE) Industrial Ethernet Switches foreseen for installation shall provide the following: - Compliance: IEEE 802.3 ISO/IEC 8802/3 - Technology: Store and forward - Filtering Services/prioritization: IEEE 802.1 D/p - Port type: Min 100 Mbps Media as necessary - Diagnostics: Indication of power status, link status, data, full duplex, link failure (fiber disconnected) - Management: SNMP, HTTP - Design: Fan less - Mechanical design: Stability against shock and vibration - Min. operating temp. range: 0°C - 70°C - Rel. humidity: 0% - 100% - Diagnostics: LEDs for indication of power status, link status, data, full duplex, link failure (fiber disconnected) - EMC: EN 55022, EN 50082-2 - VLAN support: IEEE 802.1Q, MAC Address / Port Based - MTBF: >20 years |
|  | LAYOUT OF “PV Plant SCADA, monitoring and spare room” building |
|  | An air-conditioned PV Plant SCADA, Monitoring and spare buildings shall be provided for SCADA. |
|  | All furniture for control room mounted equipment shall be supplied and shall be subject to Owner approval. All required material and civil work for installation of console for workstations in Control cum SAS room and panels for installation in Server room is in scope of bidder. |
|  | Plant control desks, system and marshalling cabinets shall be complete with all instruments and control equipment duly mounted and pre-wired. |
|  | The Bidder to submit the proposed drawing of control room building for Owner’s review. |
|  | TECHNICAL DATA SHEET |

|  | SL. NO. | DESCRIPTION | REQUIREMENT |
| --- | --- | --- | --- |
|  | 1.0 | SCADA | SCADA system shall support Modbus (TCP/IP RS-485, RTU, ASCII, IEC61850, IEC60870-5101 & 104) standard protocols (Included but not limited to) to communicate with different sub system/Devices |
|  | 1.1 | SCADA Interface | Latest OPC version 2.05a or higher compliant and implement an OPC- UA or DA 2.05a server as per the specification of OPC Foundation |
|  | 1.2 | System offered | Make / Architecture / Configuration Drawing to be enclosed |
|  | 1.3 | Year of launching of the system in the market | Bidder to specify |
|  | 1.4 | Technical Features of SCADA system |  |
|  | 1.4.1 | Operating System | Latest /As per monitoring design |
|  | 1.4.2 | UPS (2X100% Redundant or HOT STAND BY) 230 V AC, 1Ø, 50 Hz | UPS (Power supply 12-24V is required to be derived by bidder) |
|  | 1.4.3 | Power Consumption | As per monitoring design, bidder to indicate |
|  | 1.4.4 | Modules – type and Manufacturers | - Time / clock interface dev. - EIU (Electrical Interface Unit) for data acquisition - DS (Data server) - CU (Control units) - I/O Modules - Graphic Interface modules - Communication Modules - Workstation - I. Archive Server |
|  | 1.4.5 | Environmental conditions description | To be Compliant with project requirement |
|  | 1.4.6 | Minimum operation temperature | +5°C |
|  | 1.4.7 | Maximum operation temperature | +50°C |
|  | 1.4.8 | Maximum Humidity | 100% relative indoor |
|  | 1.4.9 | Cycle time Data In to command out | 10ms |
|  | 1.4.10 | PV power curtailment rate | Minimum: 10%/sec |
|  | 1.4.11 | Programming Capacity | As per monitoring design |
|  | 1.4.12 | Data handling Capacity | As per monitoring design |
|  | 1.4.13 | SCADA Precautions | RAID 5 Access per password |
|  | 1.4.14 | Response time | - Scanning rate of maximum 1 second for measurement analog signals system parameters - Loop execution time- 200 ms (max) for all loops including for CLCS input scan. - Loop execution time: 100 ms (max) for all loops including for OLCS input scan. - Scanning rate of: Programmable 50 -100 ms (max.) digital signals - Update time of 1 second or better. display OLCS / CLCS - Time for display in 1 -2 seconds. screen on operator’s request - Keyboard command to field equipment to be executed in less than 1 second. - The communication network in any case shall not be loaded more than 50% under worst case data loading - Under worst system loading conditions, the controller loading to be limited to 50% within the specified scan / loop response time and screen update times after considering all specified spare I/O channels, modules, and slots. |
|  | 1.4.15 | Auto switchover time to backup/redundant component at - Processor level - Communication level - Power supply level - I/O module level | - Transfer from main to hot standby shall be Instantaneous and bump-less. (Bidder to indicate the switchover time) - During switchover, by default, outputs shall be held stay put |
|  | 1.4.16 | Display Call up time in HMI | 1 -2 sec |
|  | 1.4.17 | Dynamic update time of parameters in the HMI monitor | 1sec |
|  | 1.4.18 | Spare Memory capacity required in the control processor (after considering spare I/O channels, modules, slots) | Minimum 40 % |
|  | 1.4.19 | Output status on controller failure | Configurable in Engineering station |
|  | 1.4.20 | Output status on power supply failure | Configurable for switching to fail safe mode |
|  | 1.4.21 | Status indication for each channel in card | LED indication required |
|  | 1.4.22 | Power supply healthiness status in all modules | LED indication required |
|  | 1.4.23 | Optical Isolation for DI / DO | Required |
|  | 1.4.24 | Galvanic isolation for AI / AO | Required |
|  | 1.4.25 | Spare capacity in RAM | Minimum 40 % including spare I/O |
|  |  | Processor Redundancy | Dual redundant hot stand-by |
|  |  | Software | Required software including application software, MIS software, HMI software |
|  | 1.4.26 | Battery backup for RAM | Rechargeable Ni. Cd /Flash RAM |
|  | 1.4.27 | Duration of battery backup for dynamic memory | 72 Hrs. |
|  | 1.4.28 | Server | - Industrial grade server - Based on latest state of art Servers - Technology suitable for Power Plant Requirement - Redundant Power supply - Redundant Communication controllers - Power Fail Auto Restart (PFAR) - Rack / blade / Tower type Redundant and HOT STAND BY server with dual power supply port - Operating system- /latest - Antivirus & MS office software- Latest - No of HDMI & VGA ports: 1 (Minimum) - RAM- 8 GB RAM or better - Hard disc-Min. 1 TB hard, RAID 5 configuration - Processor: 64-bit server grade Xenon or equivalent, Octa core minimum - Processor speed- 3.1 GHZ, 64 bits - Monitor-24” inch and 50” inch LED MONITOR - No: of USB port: 2(minimum) - No: of Ethernet port: 4(minimum) - DVD R/W feature - Storage Capacity=1 year |
|  | 1.4.29 | Communication Port | - Modbus RTU - TCP/IP - Ethernet 60780-5-104 - RS 232 - RS 485 - OPC RDI - Others: to be named |
|  | 1.4.30 | I/O modules | Online insertion/replacement of modules to be supported |
|  | 1.4.31 | Signal type analog (Type and quantity to be named) | 4 – 20 mA 0 – 10 V Others to be named Galvanically separated Resolution: 12 bits Number of inputs /outputs per card |
|  | 1.4.32 | Signal type digital / binary | Voltage rate: Contacting loads: Number of inputs /outputs per card |
|  | 1.4.33 | Cable connection | Terminated screwed Wire wrap Plug In Others: |
|  | 1.4.34 | Maximum number of channels in I/O modules - | Analog I/O modules - 16 Channels RTD, Thermocouple - 16 Channels Digital I/O modules - 32 Channels |
|  | 1.4.35 | Power supply to the field transmitters / | Analog input module shall drive the connected field transmitter on 2 wire loops |
|  | 1.4.36 | Interrogation voltage for Digital signals | 24 V DC |
|  | 1.4.37 | USB ports on Operator station | 4 no’s (minimum) |
|  | 1.4.38 | Displays on HMI monitor | Process mimic displays, trend displays, system status, alarm displays, logs / reports etc. |
|  | 1.4.39 | Minimum no of plant mimics | 75 |
|  | 1.4.40 | Time activated logs | Periodic logs, shift report, daily report, status change log, Control system fault log etc., |
|  | 1.4.41 | SER / Annunciation System | Integral SER with one m sec resolution for 256 points, Integral Annunciation with HMI display. |
|  | 1.4.42 | Password protection | Included |
|  | 1.4.43 | Programming language | English |
|  | 1.4.44 | Printers | One (1) number A4 printer colour laser jet printer, |
|  | 1.4.45 | Interface with Other systems | Through redundant, proven Industrial communication links |
|  | 1.4.46 | Spare Channels in I/O Modules | 10 % (wired up) spare channels over the entire population of each type of module. |
|  | 1.4.47 | Spare slots in the I/O rack | 20% additional slots in each rack |
|  | 1.4.48 | Fuse for I/O channels | Individual for analog signals Group of max 8 for digital channels |
|  | 1.4.49 | Diagnostics | As per monitoring design/Extensive self-diagnostic features to monitor completely the software and hardware faults in the system. Hardware diagnostic up to card/component level shall be provided. |
|  | 1.4.50 | Test facilities | included |
|  | 1.4.51 | Interposing Relays. | 24 V DC with freewheeling diode across the coil – Relay contact rating shall be 5A at 240 V AC |
|  | 1.4.52 | Cabinets to be in control room | Self-Standing type with maximum height of 2200mm |
|  | 1.4.53 | Height /Width/Depth | Bidder to specify |
|  | 1.4.54 | Weight | Bidder to specify |
|  | 1.4.55 | No. Of cabinets | Bidder to specify |
|  | 1.4.56 | Construction | Steel ,19” rack mounting |
|  | 1.4.57 | Mechanical features of PLC cabinet | a) Minimum 2mm thick CRCA b) 3mm removable gland plate c) 2.5 mm thickness for double doors d) door switch operated light e) Fans f) IP31 in A/C rooms and IP65 enclosure outdoor g) Smoke detector in PLC cabinet h) All accessories as required |
|  | 1.4.58 | Panel Earthing | Separate Safety earth for enclosure and electronic earth for electronic modules with dedicated earth pits. |
|  | 1.4.59 | Quality Assurance | As per OEM quality plan to be approved by the Purchaser / Consultant |
|  | 1.4.60 | Remote interface to OEM facility etc., | Wireless communication if required |
|  | 1.4.61 | Factory Inspection Requirements | Integrated test at factory for SCADA, PLC, HMI, Printer |
|  | 1.4.62 | Approved makes of PLC | SCADA system, including PLC shall be of the same make based on Owner’s approved make. |
|  | 1.4.63 | Software | - All necessary software required for implementation of control logic, operator station displays / logs, storage & retrieval and other specified functional requirement shall be provided. - All system related software including Real Time Operating System, File management software, screen editor, database management software, online diagnostics/debug software, peripheral drivers, software, serial link software, remote interface software and latest versions of standard PC-based software and latest WINDOWS based packages etc. - Soft l link software, Remote interface software, etc., which shall comply with the requirements on the other side. - ABT software, MIS software, as applicable |
|  | 1.4.64 | Industrial standard Serial Links | As specified |
|  | 1.4.65 | Number of Controllers | Bidder to specify |
|  | 1.4.66 | SCADA Electrical function requirements: - Control - Interlocking function - Emergency operation - Graphic mimic display - Synchronism & Energizing check - Analog measurements - Event Recording function - Disturbance Recording - All 33kV Switchgear Feeder protection functions |  |
|  | 1.4.67 | Network Management system: - Configuration Management - Fault Management - Performance Monitoring |  |
|  | 1.4.68 | Redundant Armoured 8 core minimum Fibre optic cables shall be supplied for the Redundant FO ring. CAT-6 Ethernet cable to be provided wherever applicable for local wiring within the building only. |  |
|  | 1.4.69 | Ethernet switch/Network switches: - Redundant, Manageable type - Redundant power supply - Min 2 no’s of spare port - Min refresh rate of 1 sec - Shall accept both IEC 61850 as well as Modbus TCP/IP, RTU network |  |
|  | 2.0 | GPS Master Clock system |  |
|  | 2.1 | Make & Model no. Latest make and model supports SNTP |  |
|  | 2.2 | The system shall be linked to Global Positioning satellite and shall include GPS antenna, GPS receiver, comparator units, signal processing & multiplexing unit etc. Accuracy +/- 1μSec or better. |  |
|  | 2.3 | System shall be with redundant configuration: i. GPS Receiver: Microprocessor based ii. Tracking method: Code / Carrier tracking iii. Output data format: NEMA 0183 iv. Communication speed: > 9600 BPS v. Output rate: every second vi. Signal Processing Unit: Microprocessor based Digital type vii. Overvoltage Protection |  |
|  | 3.0 | Operator / Engineering Stations |  |
|  | 3.1 | Monitors | Full HD LED Min. 24inch for engineering and 50 inch for operator station No: of USB port: 2 No of HDMI and VGA ports: minimum 1 port each Refresh rate- min 75 Hz Graphic Memory: 16 MB |
|  | 3.2 | Keyboard | Qwerty type (ASCII) |
|  | 3.3 | Mouse | Optical type |
|  | 3.4 | Slots and devices | DVD 16X or higher USB SDHC Others to be named |
|  | 3.5 | Interfaces | Ethernet: 4nos built in ethernet network port Graphic interfaces Printer Modems Serial Bus: 2 nos. Expansion Slot: 2 nos. Others to be named |
|  | 3.6 | CPU | Processor: 64-bit server grade Xenon or equivalent, Octa core minimum Type: 62 Bit, RISC based, consisting of measurement system, interlock and protection system, sequence control, closed loop control, etc. Clock freq: Bidder to specify Make and type: Bidder to specify |
|  | 3.7 | Workspace (RAM) | Minimum 16 GB RAM (upgradable up to 24 GB minimum) capacity shall meet all the process functional requirements, response requirements, I/O requirement including the spare philosophy specified. (Spare capacity in RAM Minimum 40 % including spare I/O). Make and type: Bidder to specify |
|  | 3.8 | HDD | HDD capacity: 1 TB minimum RAID HDD make and type: Bidder to specify |
|  |  | Software | M.S Windows (latest), MS Office Editor (Excel, Word, Power Point), Adobe Acrobat, Anti-virus, Network Security, etc. |
|  | 4.0 | FOCSs and ODFs: |  |
|  | 4.1 | Cable: |  |
|  | 4.2 | Type of cable | Armored type Single mode Multimode |
|  | 4.3 | No of fibers | According to monitoring design |
|  | 4.4 | Cable abbreviated designations | According to monitoring design |
|  | 4.5 | Switches/Patch panels | According to monitoring design |
|  | 4.6 | Manufacturer | Bidder to specify |
|  | 4.7 | Type | 19” |
|  | 4.8 | Bandwidth | 100MHz |
|  | 4.9 | No. of ports | According to monitoring design |
|  | 4.10 | ODF ports connector type | ST, SC, FC/PC |

- TIME SYNCHRONISATION EQUIPMENT

- The bidder can take time synchronization signal from PSS-2 GPS system through Optical Fiber Cable on OPC, for this required hardware/software/cables etc. shall be in scope of bidder.

- Bidder can supply his own Time Synchronization equipment and shall be in the Control Room.

- It shall receive Coordinated Universal Time (UTC) transmitted through Geo Positioning Satellite (GPS) for time synchronization of all components of the SCADA.

- It shall be complete in all respects including antenna, all cables, processing equipment, etc.

- All auxiliary systems and special cables required for synchronization of the equipment shall be supplied and commissioned by the Bidder.

- It shall work from DC supplies only and the Bidder to clarify if any built-in battery backup is provided, in which case, same shall be of long-life lithium batteries.

- It shall be immune to hostile electrical environment. Suitable protections are to be provided against lightning surges and over-voltages in power supply systems and antenna feeders.

- The system shall be fully tested to the relevant international standards such as IEC: 801 and IEC: 255.

- All components of the SCADA, Workstations, and all numeric protection relays, ABT meters, MFMs etc. as per requirement under this scope of technical specification or offered by bidder shall be synchronized with an accuracy of 1ms.

- The GPS shall be synchronized with the SCADA system to be supplied under this contract. Necessary software and Hardware (including laying of communication cable) required for time synchronization with SCADA and all other devises shall be in scope of Bidder.

- The system should be able to track more than 1 satellite at a time to ensure no interruptions of synchronization signals.

The system shall have provisions for combination of any of the following output signals:

- NTP (network time protocol) 100Mbits Ethernet port IRIG-B00x (TTL, pulse width modulated signal) x Pulse per half-hour/ Pulse per minute/ Pulse per second outputs via potential free contacts. Any other output port as may be required for the offered system. Alarm status contact indicating healthy status of system.

- These output ports shall be compatible with the requirement of the equipment to be synchronized as per scope of the specification. The master clock in control room shall also be synchronized with the time synchronization system. The actual port requirements (no./type) in line with the system offered shall be finalized during detailed engineering.

- The equipment should have a periodic time correction facility of one-sec. periodicity. The equipment shall also have real time display in hour, minute, second (24-hour mode) and have a separate time display, having display size of approx. 144mm height.

- Technical Specification for Network Firewall

These are minimum features additional feature shall be finalized during detailed engineering

| Technical Requirements for Network Firewall |  |  |
| --- | --- | --- |
| Sr .NO | Feature | Required Parameter |
| A | General |  |
| 1 | Common criteria certification | The offered product series or its operating system series must have achieved EAL (Evaluation Assurance Level) certification of EAL4 or higher in the common criteria for Information Technology Security Evaluation (ISO/IEC 15408) for computer security certification. |
| 2 | Architecture | The firewall shall be a purpose build hardware application based next generation firewall (NGFW) solution having application awareness & intrusion prevention function. |
| 3 | End of sale | OEM end of sale declaration shall not have been released for the offered model at the time of bid submission |
| B | Hardware Specification & Performance Parameter |  |
| 1 | Firewall Interfaces | Minimum four or as required no’s of gigabit 10/100 base T Ethernet ports to be provided |
|  |  | Provision of addition of at least Two Nos of gigabit fibre SFP ports shall be available |
|  |  | Each port must be configurable flexibly in any security zone as per the requirement without any fixed zone assignments |
|  |  | All the above specified interfaces shall be firewall interfaces. Internal Switch interfaces shall not be considered. |
|  |  | The firewall shall not have any wireless interfaces |
| 2 | Security Zones | At least four security zones must be supported |
| C | Firewall Inspection |  |
| 1 | Application Support for Inspection | Should support Standard Protocols |
|  |  | Internet based applications like Telnet, FTP, SMTP, http, DNS, ICMP etc. Should be supported for filtering |
|  |  | Internet web 2.0 application and widgets |
| 2 | NAT & PAT | Dynamic NAT as well as one-to-one NAT |
|  |  | Port/IP Address Forwarding |
|  |  | PAT |
| 3 | Resistance to Evasion | The firewall shall be able to detect and block evasion techniques including SYN flood, address spoofing and TCP split handshake etc. |
| D | Application awareness |  |
| 1 | Application intelligence and control | Firewall should support detection of application regardless of port, protocol etc |
|  |  | Firewall must identify and control applications sharing the same session |
|  |  | The firewall should allow creation of securities policies to identify, allow, block, or limit an application regardless of port, protocol etc |
| E | Intrusion Prevention System (Integrated with firewall) |  |
| 1 | General | The IPS must provide intrusion prevention functionality out of the box |
|  |  | The IPS should be capable of accurately detecting intrusion attempts and discern between the various types and risk levels, including unauthorized access attempts, pre-attack probes, suspicious activity, vulnerability exploitation etc |
|  |  | The IPS should provide protection from Advanced Botnets, inbound and outbound |
|  |  | The IPS should use stateful detection and prevention techniques and provide zero-day protection against worms, Trojans, Spyware, Keyloggers and other malware from penetrating the network |
| 2 | Detection Methods | The offered solution should use the following methods for detection of malicious traffic. |
|  |  | Signature based detection |
|  |  | Statistical Anomaly based detection |
| 3 | Threat Intelligence and signature updates | The IPS OEM should have a 24X7 security service update and should support real time signature update of the system as soon as updates are released |
| 4 | Exception List | The IPS should support the creation of Access Control List to bypass the inspection of any specific flow |
| 5 | DoS/DdoS protections | The offered solution should be capable of preventing Denial of service and distributed denial of service attacks |
| 6 | Threat Control Features | The offered solution should provide the following security features |
|  |  | Detection and blocking malicious web traffic on any port |
|  |  | Capability of detecting attacks within protocols independent of port used |
|  |  | IPS sensor should allow the admin to create IPS policies on the basis of IP address and range |
| 7 | Signature Tuning | The offered solution should allow enabling/disabling of each individual signature. Each signature should allow granular tuning to suit user requirement |

- System Spare Capacity:

- Over and above the equipment and accessories required to meet the fully implemented system as per specification requirements, Control System shall have spare capacity and necessary hardware/equipment/accessories to meet the following requirement for future expansion at site:

- 10% spare channels in input/output modules fully wired up to cabinets TB.

- Wired in “usable” space for 10% module in each of the system cabinets for mounting electronic module wired up to the corresponding spare terminals in the system cabinets.

- Empty slot between individual modules/group of modules, kept for ease in maintenance or for heat dissipation requirement as per standard practice of the Bidder shall not be considered as wiring “usable” space for I/O modules.

- Terminal assemblies (if any offered) corresponding to the IO module shall be provided for above mentioned 20% blank space.

- Each processor/controller shall have 20% spare functional capacity to implement additional functional blocks, over and above implemented logic/loops.

- Further, each processor/ controller shall have spare capacity to handle minimum 20% additional input/output for each type including above specified spare requirements, over and above implemented capacity.

- Each of the corresponding communication controllers shall also have same spare capacity as that of processor/controller.

- The data communication system shall have the capacity to handle the addition mentioned above.

- 10% spare relay of each type and rating mounted and wired in the cabinets TB.

- All contact of relay shall be terminated in the terminal block of the cabinet.

- The spare capacity as specified above shall be uniformly distributed throughout the cubicles.

- The system design shall ensure that above mention addition shall not require any additional controller/processor/peripheral drives in the system delivered at site.

- Further, these additions shall not deteriorate the system response time/duty cycle, etc. From those stipulated under this specification.

- SCADA PANEL/CABINET/CONTROL DESK/FURNITURE

- The SCADA cabinets shall be IP-22 or better protection class.

- The Bidder shall ensure that the packaging density of equipment in these cabinets is not excessive and abnormal temperature rise, above the cabinet temperature during normal operation or air-conditioning failure, is prevented by careful design.

- The Bidder shall ensure that the temperature rise is limited to 10 deg. C above ambient and is well within the safe limits for system components even under the worst condition and specification requirements for remote I/O cabinets.

- Ventilation blowers shall be furnished as required by the equipment design and shall be soundproof to the maximum feasible extent. If blowers are required for satisfactory system operation, dual blowers with blower failure alarm shall be provided in each cabinet with proper. Suitable louvers with wire mesh shall be provided on the cabinet.

- The cabinets shall be designed for front access to system modules and rear access to wiring and shall be designed for bottom entry of the cables for control room.

- The cabinets shall be totally enclosed, free standing type and shall be constructed with minimum 2 mm thick steel plate frame and 1.6 mm thick CRCA steel sheet or as per supplier's standard practice for similar applications, preferred height of the cabinet shall not higher than 2200 mm. The cabinets shall be equipped with full height front and rear doors.

- The floor mounting arrangement for other cabinets shall be as required by the Owner and shall be furnished by the Bidder during detailed engineering. Wall mounted cabinet is acceptable for Inverter room/sub-pooling switchgear.

- Cabinet doors shall be hinged and shall have turned back edges and additional braking where required ensuring rigidity. Hinges shall be of concealed type.

- Door latches shall be of three-point type to assure tight closing.

- Detachable lifting eyes or angles shall be furnished at the top of each separately shipped section and all necessary provisions shall be made to facilitate handling without damage.

- Front and rear doors shall be provided with locking arrangements with a master key for all cabinets. If width of a cabinet is more than 800 mm, double doors shall be provided.

- Two spray coats of inhibitive epoxy primer-surface shall be applied to all exterior and interior surfaces.

- A minimum of 2 spray coats of final finish colour shall be applied to all surfaces. The final finished thickness of paint film on steel shall not be less than 65-75 micron for sheet thickness of 2 mm and 50 microns for sheet thickness of 1.6 mm.

- The Preferable finish colours for exterior and interior surfaces shall conform to following shades:

- Exterior: - As per RAL 7035 (End panel sides RAL 7035)

- Interior: - Same as above

- Paint films which show sags, checks or other imperfections shall not be acceptable. As an alternative, single coat of anodic dipcoat primer along with single textured powder coating with epoxy polyester meeting the thickness requirement is also acceptable

- Control desk shall be free standing tabletop type with doors at the back and shall be constructed of 2 mm thick CRCA steel plates. A 19 mm thick wooden top shall be provided on the desk to keep the monitors at top and computers inside. Control desk shall consist of vertical, horizontal, and base supports with their coverings for work surface, keyboard trays, mouse pads, monitor shelf and concealed cable and wire way management, perforated trays with covers in both horizontal and vertical directions. ASCII Keyboard shall be capable of being pulled out through a tray.

- Bidder shall provide the two power supply feeders (DC supply or UPS AC) and one raw supply feeder of suitable rating to cater all the load requirements of SCADA panel/cabinet/control desk. System remains in service in case of single power supply failure/power supply module failure. Suitable alarm shall be generated in case of any power supply failure.

- The cabling/wiring between monitor and CPU power supply cable etc. shall be aesthetically routed and concealed from view.

- Chairs Industry standard revolving chairs with wheels and with provision for adjustment of height (hydraulically/gas lift) shall be provided for the operators and other personnel in control room area. These shall be designed for sitting for long duration such that these are comfortable for the back. Armrests in one piece shall be of polyurethane and twin wheel castor of glass filled nylon.

- Required numbers of Printer Table made of Laminated Wood or Heavy Duty MDF shall be provided for printer.

- All the furniture shall be of reputed make (Godrej or Equivalent).

- FACTORY ACCEPTANCE TEST (FAT)

- FAT procedure shall be submitted by bidder for GIPCL approval and after approval of FAT procedure, FAT will be witnessed by GIPCL Engineering or authorized representative of GIPCL.

- SCADA shall communicate with all third-party devices which are part of Solar Plant and the same shall be demonstrated during the FAT. ROUTINE TESTS: All acceptance and routine tests as per the specification and relevant standards shall be carried out. Charges for these shall be deemed to be included in the equipment price

- The manufacturer is to furnish a detailed Quality Plan indicating the practice and procedure along with relevant supporting documents.

|  | DRAWINGS/DOCUMENTS FOR APPROVAL |
| --- | --- |
|  | 7.1 Concept Note for SCADA design 7.2 Technical specification / Datasheet for SCADA 7.3 SCADA configuration drawing / system architecture drawing including HMI and third-party interface details 7.4 Control room layout 7.5 Input / Output list (SCADA I/O list) with Alarm/SER points 7.6 Hardware and software design manual of SCADA engineering 7.7 Factory Acceptance Test (FAT) procedure / SAT / Availability test procedure /PG test procedure for SCADA equipment. 7.8 Process and Electrical mimics 7.9 List of logs with point assignment 7.10 Power supply and earthing schemes (Typical) 7.11 Interconnection cable schedule (ICS) and cable schedule 7.12 QAP for all major equipment including SCADA. 7.13 GA / IGA drawings of control desk / panel 7.14 Spares list 7.15 Functional Design specification (including Graphic philosophy, design basis) 7.16 Bill of material for SCADA panel, HMI, Network components 7.17 Datasheet for all bought out items |

- Drawing/Models/Documents required for First Time Charging

- Make of PPC

- Datasheet of PPC

- Block diagram of PPC with controller transfer function with suitable parameter sets and the technical documentation for PSSE

- PSS/E MODEL OF GENERIC CONTROLLER FOR PSSE 34 VERSION

- PSSE manual shall be available in English along with OEM model

- *Dyr File of The PPC For Psse Modelling for PSSE 34

- Bidder shall address all the queries of CTU/RLDC with respect to reports and models are answered to their satisfaction.

## B10 – COMMUNICATION CABLE

- FIBER OPTIC CABLE

|  | FIBER OPTIC CABLE |  |
| --- | --- | --- |
|  | Depending on the requirements, armored single mode with minimum 12 fibers shall be used. If required, indoor fiber optic cable shall also be used as required. Optic Fiber cable shall be of maximum possible continuous length, to avoid joint between termination points as joints shall not be accepted. Bidder shall order the length of optical fiber cable per drum accordingly. |  |
|  | These cables have been foreseen for the interconnection between inverters and “PV Plant, monitoring and spare buildings” (Servers) and redundant armored Single Mode minimum 12F optical fiber cables between “PV Plant, monitoring and spare buildings” (Servers) to owner PSS-2 Common Communication Panel. |  |
|  | Through the fiber optic (MM F.O. 8 wires 62.5/125) the data collected from the power stations, meter and weather stations will be carried to Main switch panel into the Main Control box located at control room. |  |
|  | The manufacturing, construction, labeling and testing of the fiber optic cable system shall meet the requirements established in the relevant applicable ITU and IEC codes, standards and recommendations. |  |
|  | The fiber optic cables shall be moisture, chemical, and rodent protected and no splicing is permitted. The recommended fiber types are: - Over 800m distance mono mode (SM) 8 fibers. |  |
|  | The fiber optic cable shall be rated for use under the prevailing environmental conditions. The fiber optic cable shall be installed in conduits buried underground. To meet such conditions, a fully dielectric fiber optic cable rated for ducted or direct buried applications, filled with compound to prevent axial and longitudinal ingress of water and/or soluble. The cable shall have loose tubes as secondary coating of fibers. |  |
|  | The fiber cables shall be able to withstand temperature cycling in the range -10°C to +60°C without changing the optical values during laying, installation, stocking, and transportation. |  |
|  | Fiber optic cables shall have no metal screening material but shall be suitably protected against damage by vermin and shall have a waterproof self-healing membrane. |  |
|  | Fiber optic installation methods, performance, and testing shall be to ISO/IEC 1476-3, ISO/IEC 11801, and ISO/IEC 24764 specifications. |  |
|  | Fiber optic cables shall be carefully protected and isolated from the environment within which they are installed. For example, fiber optic cables shall be protected against mechanical and chemical damage due to micro cracking caused by stones, acid soils, and over bending. |  |
|  | Fiber optic cable placement and interim storage shall also be in accordance with the manufacturer's recommendations. |  |
|  | Technical descriptions detailing the fiber optic cable performance shall be provided. |  |
|  | CODES AND STANDARD |  |
|  | Standards not indicated in the specification are acceptable subject to approval by the PURCHASER/PURCHASER’s Consultant if they are established to be equal or superior to the standards indicated in the specification. In case of conflicts between the standards and this specification, this specification shall govern. |  |
|  | Codes | Description |
|  | IEC 60794/IEC 60793 & EIA/TIA 455. | Fiber optic cable |
|  | IEC 1034 | - Low smoke -light transmittance of 80%). |
|  | IEC 754 | Halogen free 1&2- maximum acid gas generation shall be 2% by weight and PH >4.3 |
|  | IEC 331, IEEE 383 | Fire & flame retarded |
|  | EIA -455-41 | Crush Resistant |
|  | EIA -455-25 | Impact Resistant |

|  | Standards not indicated in the specification are acceptable subject to approval by the Purchaser/Purchaser’s Consultant if they are established to be equal or superior to the standards indicated in the specification. In case of conflicts between the standards and this specification, this specification shall govern. |
| --- | --- |
|  | ### DESIGN CRITERIA |
|  | ### UNDERGROUND FIBER OPTIC CABLES - Underground approach fiber optic cable shall be of a loose tube type, with the fibers overfed into buffer tubes which are helically wound around a central strength member. The buffer tubes shall be composed of a suitable polymer and be sufficiently strong to hold their shape and provide protection for the optical fibers against deformation and friction. The buffer tubes shall be fitted with a suitable water blocking compound which shall not freeze or drip out over the temperature range specified for the site. The compound shall not be detrimental to the other cable elements, shall not cause swelling of the buffer tubes, and shall have a relatively low thermal expansion coefficient. The compound shall also be easily removed from the fiber and shall be non-toxic. - The central strength member of the cable can either be of glass reinforced plastic (GRP) type where a metal-free cable is required or a steel wire. - The fiber optic cable shall be designed so that the fibers shall be free from longitudinal strain under all conditions of loads and ambient temperatures specified. The design of the fiber optic cable shall be such that an extension of 0.6% will not produce strain in the fibers and not result in an increase in attenuation. - The fiber optic cable shall be rated to operate at the continuous and intermittent short-term temperatures without degradation of its mechanical or optical performance. The surface of the cable jacket shall be designed to minimize the accumulation of dust and shall resist abrasion. - Polyethylene is the preferred material for sheathing outdoor cables. The use of a laminated aluminum PE sheath is acceptable. The cable shall withstand longitudinal water penetration when immersed to a depth of 1 meter in water at a temperature of 200 ºC for a period of 24 hours and under the conditions specified in IEC 60708. - Armoring shall be used for all direct buried cables or for cables requiring rodent protection. This shall comprise at least one layer of galvanized steel tape 0.2 mm thick, steel laminated sheath applied directly to the cable core, or a fiberglass braid. All armoring shall be protected from corrosion and damage by a polyethylene sheath. |
|  | ### INDOOR FIBER OPTIC CABLES - Fiber optical cables for indoor use shall be of the tight buffered or composite buffered construction in which the fibers are encased in a tight buffer of a suitable plastic material. All indoor cables shall be metal free and unfilled. The central strength member shall be composed of a glass reinforced plastic material (e.g. Kevlar) or aromide yarns. - Indoor optical fiber cable sheaths shall be made from halogen free resistant polymers and shall comply with the standard for flame retardant cable material specified by IEC 60332. |
|  | ### Fiber optic cable accessories: - A detectable reinforced underground marking and warning tape shall be laid in the ground 300 mm above the protection conduit. - The patch cord consists of a single/multi-phase fiber optic cable with plug connections on both ends. Pigtails are fiber cables pre-assembled with a connector at one end. The fibers of the patch cords and pigtails shall be according to the specified fibers and all components shall have a service life of more than 20 years with a minimum of contact durability of 1000. - OTDR (Optical Time Domain Reflectometer) test report shall be submitted to Client. |
|  | ### CABLE DRUMS - Cables shall be supplied in non-returnable wooden drums. The wood used for construction of the drum shall be properly seasoned and free from defects and wood preservative shall be applied to the entire drum. All ferrous parts shall be treated with a suitable rust preventive coating to avoid rusting during transit or storage. - The BIDDER shall indicate in the offer, the maximum length for the size of cable, which can be supplied on one drum. The actual length supplied on each drum shall be within tolerance limit of 5 % with an overall ceiling of +5% on total ordered quantity of each size of cable. - Cable drums shall carry following details in printed form: - Manufacturer’s name and trademark - Type of cable and voltage grade - Year of manufacture - Type of insulation - No. of cores and size of cables - Cable code - Length of cable on drum - Inner Diameter and Outer Diameter of Drum |
|  | ### OPTICAL FIBER JOINTS - Each cable joint shall include termination box, mounting hardware, optical fiber splice kits, cable entry seals, and all accessories required to produce a permanent optical joint. Details of the proposed optical fiber joints shall be submitted for the approval. - Each termination box shall be capable of being hermetically sealed after jointing, and hermetically sealed after re-opening. - Variations in the quality of workmanship in making the fusion splice shall have a minimal effect on the efficiency and reliability of the joint. |
|  | ### TERMINATION - Type of connectors shall be of same type all over the plant. Bidder shall decide the used type (ST; SC; FC/PC) - The connecter loss shall not exceed 0.5 dB per connector pair. - All optical terminations between fibers and equipment or other fibers shall be made using low loss de-mountable optical connectors of the plug-in type complying with the requirements of IEC 60874. - All spare fibers shall be terminated with appropriate optical connectors and attached to a coupler. Caps shall be provided for each coupler to prevent dust ingress to the couplers of unused fibers. - All connectors shall be so positioned to facilitate easy cleaning and inspection. |
|  | ### OPTICAL TERMINATION BOXES - Optical Termination Boxes (OTB) shall be installed at sites to terminate all outdoor optical cables and to provide the interface between the outdoor and indoor optical cables. - All fibers in each optical cable shall be terminated using a terminal block or end sheath; unused fibers shall not be coiled, left unprotected or un-terminated. - The OTBs shall have the following characteristics: - The OTB shall be suitably sized for the number of cables to be initially accommodated, including space to manage and retain surplus lengths of optical fiber tails, plus 50% spare capacity. - The optical fiber cables shall enter the OTB through appropriately sized cable glands. - The OTB housing should be wall-mounted, of rugged construction and provided with fixed covers. - The OTBs shall incorporate fixed de-mountable couplers with dust caps of sufficient number to retain all the optical fibers entering the box plus space to fit 50% additional couplers. |
|  | ### Optical Fiber Distribution Frames (OFDFs) - The termination of each fiber in transmit and receive direction shall be provided on an optical fiber distribution frame (OFDF) for access to the transmission equipment. The OFDF for receive and transmit direction shall be configured in accordance to the specified number of fibers. - The OFDF are to be installed in termination cabinets, which may be combined with the communication system. - OFDFs shall be provided, as necessary, to facilitate: - The termination of optical fibers and connection of optical circuits to terminal equipment; - Testing and isolation of both the optical fiber cable and fiber optic terminal equipment; and - Provide interface and/or cross-connect facilities between different sets of optical line terminal equipment. - Sufficient space shall be available on the frame to allow ease of access and minimize the possibility of interference or damage to fibers carrying traffic during maintenance testing on the back-up or spare fibers. - Optical fibers shall be terminated by detachable connectors in the optical fiber distribution frame and shall be properly labeled with fiber identity, destination or source, go or return. It shall be possible to connect each optical fiber to the appropriate point on any terminating equipment. Fixed couplers shall be provided for each fiber comprising a link. - The following basic functions of the fiber distribution frame are required: - Circuit re-routing/jumping. - Circuit disconnection; and - Patching and test connections. - Plug-in connections shall be used and the transmit and receive direction of the transmission shall be segregated. The optical fiber tail cables and connections shall be substantially protected from possibility of damage due to maintenance or installation activity. Facilities shall be provided for termination of any metal cores within the fiber cables. - The capacity of the fiber distribution frame shall be chosen to accommodate the maximum capacity of the fiber optic communication system plus 50% spare capacity to cater for any future expansions. All fiber distribution frames shall have an earth connection provided and shall be protected from corrosion by painting or galvanizing. - Where space is limited, the functions of OTB and OFDF may be merged into a single unit provided the full requirements of both OTB and OFDF are met by that single unit. |
|  | TECHNICAL PARAMETERS |

|  | Sl. No. | Item Description | Technical Requirement |  |
| --- | --- | --- | --- | --- |
|  |  | Fiber: - The optical fiber core shall be of ultra-pure fused silica glass coated with UV cured acrylate suitable to withdraw temperature of about 80 Deg C (continuous). - Fiber Optic cables shall be suitable for installation on cable tray, duct bank, cable trench, and direct burial as necessary. - The cable should comply latest CEA technical standard. |  |  |
|  |  | Type | Single mode armoured cable |  |
|  |  | Core Diameter | 50+/- 0.015 µm |  |
|  |  | Cladding Diameter | 125 ± 2 microns |  |
|  |  | Coating Diameter | 245 µm with tolerance of +/-5 µm |  |
|  |  | Fiber Proof test | As per IEC/EIA & other International Standards |  |
|  |  | Coating Diameter Test | As per IEC/EIA & other International Standards |  |
|  |  | Number of Fibers/core | Twelve (Color Coded) with min. 100% spare core (Fibers) |  |
|  |  | Optical Characteristics Bandwidth, Attenuation & Numerical Aperture |  |  |
|  |  | Bandwidth @ 850 nm Bandwidth @ 1300 nm | 500 MHz-Km min 500 MHz-Km min |  |
|  |  | Attenuation @ 850 nm Attenuation@ 1300 nm | 3.0 dB/Km max 0.8 dB/Km max |  |
|  |  | Numerical Aperture | 0.200 + 0.015 |  |
|  |  | Optical Characteristics- Attenuation | for Single mode fiber cable outside plant: | for Single mode fiber cable inside plant: |
|  |  | Attenuation@ 1310 nm Attenuation@ 1550 nm | 0.35 dB/Km max 0.2 dB/Km max | 1 dB/Km max 1 dB/Km max |
|  |  | Cable Construction: The cable shall be of dual jacket & armored. Optic Fiber cable shall be polymer coated, Electrolytically chrome plated corrugated steel taped (ECCST) armored, fully water blocked with central dielectric material for outdoor/indoor application so as to prevent any physical damage. Two highly visible ripcords are placed under the jacket to aid in sheath removal. A co-polymer coated steel tape is corrugated and wrapped around the inner jacket to provide additional cable compression strength and Termite & rodent protection. A ripcord is also placed underneath the armor for easy outer jacket removal. |  |  |
|  |  | Outer Colour | Orange |  |
|  |  | Outer Jacket | Polyethylene minimum 1.5mm thick, Flame retardant & UV resistant. |  |
|  |  | Inner Jacket | Core-locked flame-retardant polyethylene |  |
|  |  | Filler / Strength member | As per manufacturer standard |  |
|  |  | Central Strength member | Fiber Glass reinforced plastic (FRP) and Buckle resistant material to provide both tensile and anti-bucking strength to the cable. |  |
|  |  | Life Expectancy | Fiber Optic cable shall provide a long life expectancy of minimum 20 years under continuous operation without degradation to optical or mechanical performance. |  |
|  |  | Stripping Ability | All layers easily removed with Commercially available tools |  |
|  |  | Installation: |  |  |
|  |  | Minimum bending radius | 20 X D (D=core Diameter) – During Installation, Short Term, loaded. 15 X D (D=core Diameter) Installed, Long Term, No load |  |
|  |  | Maximum Tensile Load/Strength | During Installation: 2200 N Installed: 1500N |  |
|  |  | Method of laying | Directly laid in cable trays / duct bank / clamped with available structure |  |
|  |  | Pulling | Ordinary cable grips |  |
|  |  | General: |  |  |
|  |  | Maximum Cable weight | 46Kg/1km |  |
|  |  | Maximum cable length | 1 km |  |
|  |  | Data Speed performance | 10 Gbps minimum |  |
|  |  | Test Specification (EIA/TIA) |  |  |
|  |  | Impact Resistance | 2000 Impacts minimum |  |
|  |  | Crush Resistance | 4000 N/10cm minimum |  |
|  |  | Compressive Strength | 3000 N minimum |  |
|  |  | Moisture/Water Resistance as per IEC standard. | Water blocking layer, Cable shall withstand water penetration when tested with a one-meter static head or equivalent continuous pressure applied at one end of a one meter length of filled cable for one hour. No water shall leak through the open cable end. |  |
|  |  | Optical time Domain reflectometer | - A recording optical time domain reflector meter (OTDR) will be utilized to test for end-to-end continuity and attenuation of each optical fiber. The OTDR shall be equipped with data storage, printer, help feature, compare trace features and OTDR software. The data storage unit must include a built-in floppy disk drive capable of storing a minimum of 100 test traces. - Data traces saved to disk shall include the following labels. - Fiber Identification (ID) with a minimum of 10 characters. - Cable ID with a minimum of 10 characters - OTDR location with a minimum of 20 characters - Far End location with a minimum of 20 characters. - Test operator initials with a minimum of 3 characters. - The printer shall preferable be internal. The printer shall be able to print data traces within 30 seconds or less. The machine setting used to repeat tests later shall include index, range, wavelength, average time, pulse width and scale settings. The test results (on printout) shall provide information including: loss, distance, reflectance, data and time. - The requirements for the compare trace feature include the ability to recall two historical traces from a diskette and display them simultaneously for analysis and printing. The compare trace must compute and display a single graph representing any differences between two traces. The compare trace must be able to recall historical traces from a discrete and perform the same tests on connected live fibers. The compare trace shall perform a two point loss measurement test for any two particular fibers in a comparison analysis. The losses between the two points on the each fiber shall be displayed, and the differences between the two readings clearly shown. - The OTDR must be equipped with software to support all of the required functions. The software shall provide for printing of whole set of traces (batch print) with minimal commands eliminating the time spent for printing traces individually. - Bidder shall provide all mounting accessories, cables and connectors required to establish data communication. |  |

- MODBUS CABLE

Data (Modbus) Cable to be used shall be shielded type with stranded copper conductor based on VDE 0881 . Cable shall have minimum 2 pair each with conductor size of 0.5 SQMM and core identification shall comply with DIN 47100. Cable shall be flame retardant according to IEC 60332-1-2. or equivalent Standard Surge protection device to be provided shall be approved from UL/CSA or any national/international approved lab.

- CAT6 SFTP CABLE or Lan cable or Ethernet cable

Ethernet cable must be at least of CAT5. Cables must be shielded. Length must not exceed 75 m.

| Sr.No. | Technical Parameter |  |
| --- | --- | --- |
| 1 | Category type | 6 and above |
| 2 | Conductor | 23 AWG Solid bare Copper |
| 3 | Type | Shielded with Foiled Twisted Pair |
| 4 | Pairs | 4 |
| 5 | Insulation | Special grade PE |
| 6 | Fire Characteristic standard | IEC-332 |
| 7 | Quality Certification | UL ISO - 9002 |
| 8 | Connector | Metal shielded RJ45 connector with boot caps |
| 9 | Outer sheath | Extruded FRLS PVC confirming to type ST2 of IS-5831 (Anti rodent, anti-termite & moisture resistant properties) |

- SM armored FO duplex Patch chords

| Sr.No. | Technical Specification |  |
| --- | --- | --- |
| 1 | Connector Type | SC, ST, FC, LC |
| 2 | Fiber Type | Armored Single Mode OM2 Fiber 50/125um |
| 3 | Tight Buffer Colour | White/yellow |
| 4 | Tight Buffer Material | LSZH |
| 5 | Tight Buffer Diameter (mm) | 0.9 +/- 0.05 |
| 6 | Strength Member | Aramid Yarn |
| 7 | Jacket Colour | Orange for OM1 & OM2, Aqua for OM3 & OM4 |
| 8 | Jacket Material | LSZH |
| 9 | Jacket Thickness (mm) | 0.45 +/- 0.05 |
| 10 | Cable Diameter (mm) | 2.9(+/-0.1) X 5.9(+/-0.2) |
| 11 | Minimum Bending Radius (mm) | Vendor to specify |
| 12 | Attenuation (db/km) | <= 1.5 at 1300nm, <= 3.5mm at 850nm |
| 13 | Short Term Tensile (n) | 160 |
| 14 | Crush Resistance (n/100mm) | 500 |
| 15 | Operation temperature | -20 ~ 70 |

|  | DRAWINGS/DOCUMENTS FOR APPROVAL |
| --- | --- |
|  | Master drawing list (showing all the vendor's submission schedule and revision status) |
|  | Cable reel arrangement drawing |
|  | Detailed cable laying method |
|  | Cable Drum Schedule |
|  | Dimensional detailed drawing of the cable cross-section. |
|  | Installation and termination instructions. |
|  | Catalogue of cables in colour |
|  | Material property reports |
|  | Certified copy of tests |
|  | Overall shop inspection and test schedule |
|  | Shop test and inspection procedure |
|  | Certificate of compliance to contract specification. Test Certificate from NABL accredited laboratories |

## B11 – SEM (ABT)TARIFF METERING SYSTEM

|  | SEM (Special Energy Meter) Tariff Metering System |
| --- | --- |
|  | Introduction This section covers the requirements of tariff metering system at solar generation plant as per WRLDC/ SLDC/ CTUIL / CEA Regulation / statutory requirement. |
|  | Scope of Work Scope of work shall be included following equipment but not limited to. - Special Energy Meters (ABT) and associated modem will be free supply by GIPCL to the bidder. Details shall be provided to successful bidder during detailed engineering stage. However, required TTBs, Aux. supply change over scheme with dedicated MCBs (signalling to SCADA), meter & modem with antenna installation arrangements, blanking plates (aesthetically designed), all associated wiring, integration with SCADA, required loading on UPS and DC system for sizing calculation etc. for successful commissioning of the system is in the scope of bidder. - Bidder shall provide all required arrangement for Special Energy Meter (ABT) system i.e. tariff and/or revenue and/or energy accounting metering system for each 33kV Transmission line at the solar generation plant end. - Bidder shall provide SEM (ABT) tariff metering 0.2s Class CTs, 0.2 Class PTs with sealing arrangements (CTs, PTs terminals, TTB terminals front and Back, TBs, CTs, PTs compartments, Metering compartments, Meter terminal block, meter body, etc.,). The responsibility of arranging for the CTs, PTs etc. its approval / inspection/calibration/testing charges etc. rests with the Bidder. All charges incurred on testing of CTs, PTs etc. shall be borne by the Bidder. |
|  | Deleted |
|  | TECHNICAL REQUIREMENTS General - Tariff metering systems shall meet the requirements of CTUIL GETCO, GIPCL and RLDC. - Deleted - Tariff metering system for 33kV Transmission lines shall be provided in the switchgear panel. System shall be installed by bidder as per regulatory requirements. - For current transformer (CT) and voltage transformer (VT) circuits 2.5 sq. mm copper conductor wire with FRLSH PVC insulation shall be used. Wiring shall be color coded. Current transformer leads shall be checked for lead burden, VA capacity. In case 2.5 mm2 Copper Conductor is not adequate, conductor of 4 mm2 cross section or higher shall be used. Voltage transformer leads shall be checked for voltage drop In case the voltage drop with 2.5 sq.mm copper conductor exceeds this value, higher conductor sizes shall be used. All control / auxiliary wiring shall be carried out with 1100V grade stranded min. 1.5 sq. mm copper conductor wires with FRLSH PVC insulation. - Terminal blocks shall be clip-on type 600V grade, 10A rated stud type terminals with markings. Terminals for VT secondary leads shall be stud, disconnecting type. CT secondary leads shall be provided with short circuiting and earthing facility. At least 20% spare terminals shall be provided for each terminal station and each type of TB. CT / VT test terminals shall be provided separately. - Prior to the installation of meter, the space provided for the meter at panel shall be covered by suitable blanking plates by the bidder. - The accuracy class of SEM meter (supplied by GIPCL) shall be of 0.2s class. - Deleted - Deleted. - Deleted - The CT wiring shall be of 6 wire type (i.e., Not 4 wire type) - Deleted |
|  | Following details, Functions are available in SEM (ABT) meters supplied by GIPCL free of cost to successful bidder as below: However, installation, commissioning and integration with SCADA shall be in the scope of Bidder. - There shall be provision for access to the meter by a computer (desktop, PC or laptop) and remote reading or data storage via communication system. - Not used - ABT meter all data shall be integrated to SCADA System. - Communication port: One RS 485, One Ethernet, RS 232 & front optical port and all communication ports of meter shall be available for simultaneous uninterrupted communication. - Load survey capability - Missing potential indication in case of failure of potential at the meter incoming terminal. - Provision for telemetering using common protocol - Meter to be Time synchronize with Master clock. - ABT Metering compartment shall have 230 V UPS supply for Modem. UPS supply shall have separate MCBs with signaling contacts (ON, OFF) integrated to SCADA - Auxiliary supply of each ABT Meter shall be from two sources (110 V DC Main-1 and 230V UPS Main-2) with Auto-changeover selection scheme. Each meter shall have dedicated MCBs with it's ON, Trip status monitoring at SCADA as well as at local annunciator. In case of non-availability of auxiliary supply, meter shall draw auxiliary power from PT (self-powered). - Auxiliary supply systems of ABT meters are to be monitored (NO Volt relay) in SCADA and local annunciator. - Each ABT meter shall have separate / dedicated TTB and shall be connected in such a way that it facilitates testing / checking / removal / replacement activates without affecting other ABT meter connected to same core of CT/PT. TTB shall be of 3 phase-4 wire type. TTB shall be mounted below the meter and in front of the panel. Rear side of TTB shall have tamperproof sealing arrangement. TTB shall be of large size and shall be of SCREW type (Tightening of the screw shall short the CT circuit and loosening will open the current path of CT circuit) - For 33 kV Metering CT/PT, terminals shall have proper sealing arrangements, preferably with high quality transparent polycarbonate covers. - Site testing and sealing of metering system (ABT meters and CT/PT's, TTB's, Terminal boxes, Panel doors etc.) by concerned authorizes and applicable charges, if any, is in scope of Bidder. - Terminal Block Station (TB's) shall have proper sealing arrangements. of ABT meters to be provided. - Wires to Meter terminals TTB etc. shall not be projected outside the panel. Optical port and display of meter, operating control of meters shall be easily accessible for day-to-day operation. Overall design shall be esthetically very good and highly functional. Bidder shall extend fullest co-operation to GIPCL for finalization of design in case “projection mounting meter” is required to be install (instead of flush mounted). |
|  | Submission of Laboratory and site testing reports. Test reports of instruments transformers at NABL accredited / approved laboratory and site testing reports shall be submitted to purchaser as well as to the concerned competent authority at appropriate stage |