VOLUME – II

PART – 1

SCOPE OF WORK & TECHNICAL SPECIFICATIONS

# TABLE OF CONTENTS

| Section | Description | PAGE NO. |
| --- | --- | --- |
|  | SCHEDULE-I |  |
| ----- | Scope of Work, Terminal points and Exclusions | 3 |
|  | SCHEDULE-II |  |
| ----- | Project Information | 13 |
|  | Provenness Criteria | 17 |

# SCHEDULE-I SCOPE OF WORK

|  | SCOPE OF WORK: |
| --- | --- |
|  | The scope of work includes design, engineering, construction (as per detail technical specification) manufacturing, procurement of equipment, shop testing, packing, transportation, delivery & unloading at site, storing and security at site, project management, stores management, insurance, erection, testing and commissioning of all equipment / system and post commissioning services of 500 MW AC / 625 MWp Solar PV Plant in accordance with this specification. It also includes the O&M works for period of three years. |
|  | The scope of work mentioned in this specification covers all necessary works / equipment for the project. The statements and explanations contained in this regard are intended to provide a proper understanding to Bidders but should not be construed as limiting Bidder’s responsibilities and / or Owner’s right to amend / change the scope or the terms. It shall be clearly understood that the intent of the Owner is that the Bidder shall execute this project on turnkey basis for a lumpsum fixed price subject to the terminal points explicitly identified and consequently, any omissions, conflicts or contradictions in these specifications shall be noted, interpreted and applied appropriately to give effect to this intent. No risk related to land, soil and flooding shall not be passed on to the Owner after award of contract. Claims or disputes on account of wrong interpretation or wilful misinterpretation of this intent by Bidder after award of Contract will not be entertained by Owner nor will they be legally binding on Owner. |
|  | Bidder shall visit the site and assess the complete work before submitting the Bid. |
|  | GIPCL is planning to install 8 Nos of Wind Turbine Generator (WTGs) on periphery of the plot (as per the following tentative locations). Bidder shall leave the shadow free area while preparation of Overall array layout. The Hub Diameter of WTG shall be considered as 150 Meters and hub height shall be 150 M. The exact Locations of WTGs shall be decided during detail Engineering. Bidder shall consider above WTG’s shadow to meet Targeted generation. Figure-1 |
|  | SCOPE OF SUPPLY |
|  | Except Module all supply is included in Bidder’s scope. |
|  | Bidder to ensure that the manufacturers and makes of all the equipment offered are as per List of Approved Manufacturers as specified in Schedule -IV of this specification. |
|  | Any other supply item, erection or testing required for the plant is deemed to be considered in the scope of this contract even if not specifically mentioned in this specification. |
|  | SCOPE OF WORK - ERECTION, TESTING AND COMMISSIONING |
|  | The erection, testing and commissioning of all the equipment / items for completion of the project are deemed to be included in Bidder's scope. |
|  | Unloading, storage, transportation to place of installation, erection, testing and commissioning of 625 MWp PV Modules (PV Modules will be free issue to the bidder by GIPCL at one location only) are also included in the scope of the Bidder. |
|  | Conducting Performance Guarantee (PG) tests and submission of relevant reports as per the agreed schedule and procedure under the supervision of Owner’s representative shall be included in Bidder's scope. |
|  | GENERAL REQUIREMENTS |
|  | Bidder shall comply with the following documents / guidelines: - CEA / CERC / IEGC - CEIG requirements - IE rule - WRLDC / GETCO / SLDC / RLDC /other statutory bodies |
|  | Bidder shall provide all required arrangement for Special Energy Meter (ABT) system i.e. tariff and/or revenue and/or energy accounting metering system for each 33kV Transmission line at the solar generation plant end. |
|  | Bidder shall provide SEM (ABT) tariff metering 0.2s Class CTs, 0.2 Class PTs with sealing arrangements (CTs, PTs terminals, TTB terminals front and Back, TBs, CTs, PTs compartments, Metering compartments, Meter terminal block, meter body, etc.,). |
|  | Special Energy Meters (ABT) and associated modem will be free supply by GIPCL to the bidder. Details shall be provided to successful bidder during detailed engineering stage. However, required TTBs, Aux. supply change over scheme with dedicated MCBs (signalling to SCADA), meter & modem with antenna installation arrangements, blanking plates (aesthetically designed), all associated wiring, integration with SCADA, required loading on UPS and DC system for sizing calculation etc. for successful commissioning of the system is in the scope of bidder. |
|  | The Bidder shall be responsible for complete satisfactory working of the system with guaranteed parameters. All major equipment shall be installed, tested, and commissioned under the supervision of the manufacturer’s representative of the respective equipment. |
|  | The detailed contract document and schedule of quantities covering even the minor equipment shall be worked out by the Bidder for the total implementation of the job. The technical requirements of the main equipment involved as per the scheme are covered in technical section and other appropriate sections forming part of this bid document. |
|  | The specification provided with this bidding document outlines the functional requirements. The Bidder must submit a proposal based on the functional requirements specified in the bidding documents. |
|  | Design ambient temperature shall be 50°C to be considered for design purpose for all equipment of the plant. However, for Design ambient temperature of Inverters clause no. 3.6 (inverter section) is applicable. |
|  | The Bidder shall specifically mention in case of any deviation from the scope of the work. In general, the Bidder shall ensure compliance of all provisions of the bid documents and submit their bid accordingly and shall submit an undertaking that they have not taken any deviations. |
|  | Redundant Auxiliary power system to be provided for all the system except ICOG system. |
|  | Overall plant, equipment, devices shall be aesthetically design to the satisfaction of the Owner. |
|  | The site study carried out by Owner viz., topographical survey, geotechnical survey (including liquefaction analysis), hydrology, ERT etc. shall be for information to Bidder. Bidder shall carry out their own study during detailed engineering. Such studies and activities shall be part of Bidder’s scope. Bidder is responsible for all necessary studies and activities for successful completion of project. Bidder to make necessary arrangement for construction power and water along with setting up of site offices as required for the execution of the project. |
|  | The bidder shall be carried out the comprehensive operation & maintenance (O&M) of Solar plant for 3 year and Annual Maintenance Contract (AMC) of critical equipment for period of 10 year as mentioned in clause no.05 (G) of project information after successful commissioning and performance demonstration. |
|  | Soft copies, excel files, AutoCAD files etc. shall be submitted along with calculations / drawings (without that drawing shall not be reviewed). |
|  | For finalisation of AC SLDs, following basic calculations and system studies shall be submitted - Fault level at each Bus - Insulation Coordination studies, - Reactive power sizing calculations - Any other calculations or studies required |
| 2.1 | Power Evacuation System Bidder has to terminate all the 33kV transmission lines from the Solar PV Plant at the 33/400kV PSS-2 (Pooling station-2) on allocated 33KV Bay as per system requirement to be finalized during detail engineering without any extra cost to the Owner. Tentative 33kV Feeders allocation at 33/400kV PSS-2 (Pooling station-2) for 500MW Solar PV Plant are as below: TENTATIVE 33KV TRANSMISSION LINE BAY ALLOCATION AT PSS-2. PRE-ENGINEERED BUILDING Number; Board Number; Number of Feeders (Quantity); Max. Power Injection permitted for each Board (MW); Max. Power Injection permitted for each Board (MVA); Tentative Bay Number. 3; 5; 6; 150; 170; 32503. 32504. 32505. 32506. 32507. 32508. 3; 6; 6; 150; 170; 32603. 32604. 32605. 32606. 32607. 32608. 4; 7; 4; 50; 56.67; 32705. 32706. 32707. 32708. 4; 8; 6; 150; 170; 32803. 32804. 32805. 32806. 32807. 32808. Total; 22; 500; 566.67. - All above feeder rating is 1250 Amp, 31.5 KA @ 50 deg C. - Cables to be terminated at Panel-B(Metering Panel). - The total Generation capacity (MW, MVAR & MVA) shall be distributed in balance manner i.e. equally to each LV windings of 400/33/33 KV Transformers. Generated Power from 500MW solar project shall be finally pooled to 33/400kV PSS-2 (Pooling Sub Station-2). These 33 kV Transmission lines shall be either from sub pooling stations and/or directly from Inverter stations / blocks or combination of both (sub-pooling or directly). Please refer Electrical Key SLD as per attached Annexure-1. “Only Utilization of Space” for Two Numbers of 33kV transmission line bays (i.e. two numbers of breaker panels and two numbers of associated SEM metering panels) is available at each 33kV boards (Board Number 5, 6, 7 & 8) of PSS-2 (Maximum 8 Numbers of 33kV transmission line bays can be accommodated in PEB 3 & 4). Bidder may opt for utilization of space available for 33kV transmission line bays at PSS-2 subject to compliance of specifications, details, drawings and scope mention at Annexure – 9. Details of “Only Utilization of Space” available for 33kV transmission line bays at PSS-2. Pre-Engineered Building Number; Board Number; “Only Utilization of space” available for Number of TL Feeders (Quantity); Tentative Bay Number. 3; 5; 2; 32511. 32512. 3; 6; 2; 32611. 32612. 4; 7; 2; 32711. 32712. 4; 8; 2; 32811. 32812. Total; 8. Note :. Maximum power (MW, MVAR & MVA) injection permitted for each board shall be as mentioned in table "TENTATIVE 33KV TRANSMISSION LINE BAY ALLOCATION AT PSS-2". |
|  | Telemetry System |
|  | The arrangement to transmit data required by the Load Dispatch Centre (LDC) from Solar plant to WRLDC/SLDC as per extant regulations and procedures for grid management. |
|  | The required hardware and software, including laying and termination/splicing with all required connectors etc. of Communication/Fibre Optic cable to Owners’ common communication panel at 33/400kV GIS Substation required for communication of Solar plant data is included in the Bidder’s scope. Communication link and communication controller/Gateway used for data communication to common communication panel /LDC shall be redundant (one for normal operation and other as hot standby). If any upgradation/ modification required at FOTE, it shall be done by the bidder. |
|  | Bidders are advised to update themselves with RLDC / LDC / SLDC requirement for compliance related to Automatic Meter Reading (AMR), telemetry data, channel and procedures for engineering of telemetry solution accordingly. |
|  | The above real time data communication facility with RLDC/ LDC/ SLDC shall comply CERC (Communication System for Interstate Transmission of electricity) Regulation 2017, Procedure for Implementation of the Framework on Forecasting and Scheduling for Renewable Energy (RE) Generating Stations, CEA (Technical Standards for Communication System in Power Systems Operations) Regulations, 2020,CEA Guidelines on Cyber Security in Power Sector 2021, CEA Manual of Communication Planning In Power System Operation 2022, Grid India Draft Detailed procedure covering modalities for first time energization and integration of new or modified power system 2023and amendments thereof. |
|  | Telemetry system shall provide real time data for solar plants for all parameters. mentioned in Annexure- VII(B), VII(D), sample profile of IEC 104 VII (F) of Grid India Draft Detailed procedure covering modalities for first time energization and integration of new or modified power system 2023 to the respective RLDC @ resolution of 4-6 sec. |
|  | TERMINAL POINTS |
|  | Electrical - Bidder has to terminate all the 33kV transmission lines from the Solar PV Plant at the 33/400kV PSS-2 (Pooling station-2). All hardware required for 33kV cable termination at 33/400kV switchyard, including support structure/buildings and civil works required for the same, shall be under scope of bidder. |
|  | EXCLUSIONS |
|  | Supply of following equipment are excluded from the scope of the Bidder: |
|  | - 33/400kV Power transformers - 400kV Switchyard - 33kV Main Switchgear at PSS-2 (limited to feeders as mentioned in the above table of “TENTATIVE 33KV TRANSMISSION LINE BAY ALLOCATION AT PSS-2”) - Pooling substation Main Control Building - Periphery Road Lighting - Solar PV Modules - Peripheral road - Phasor Measuring Units (PMU) - Special Energy Meters (ABT) and associated modems. - 8 Nos. of WTGs planned along the Boundary by GIPCL |
|  | Tests |
|  | Type Test All equipment to be supplied shall be of type tested design. During detailed engineering, the Bidder shall submit for Owner's approval the type test reports of all equipment. The time validity of the reports shall be as per CEA standard guidelines. For equipment where type test validity is not mentioned in CEA, Bidder to ensure the type testing is within 5 years from the LOA date. All type test reports shall be from NABL Accredited laboratory /CPRI. |
|  | Routine Test All acceptance and routine tests as per the specification and relevant standards shall be carried out. Charges for these shall be deemed to be included in the equipment price. An indicative list of tests / checks mentioned in respective specification. However, the manufacturer is to furnish a detailed Quality Plan and MQAP, CEA Guidelines for Model Quality Assurance Plan (MQAP) for Major equipment of Power Sector and in line with relevant standards indicating the practice and procedure along with relevant supporting documents. |
|  | STATUTORY COMPLIANCE, GRID CONNECTIVITY AND POWER EVACUATION - Bidder shall comply all provisions and amendments including but not limited to the following. Further all the charges and approvals for commissioning and O&M of the plant is in the scope of Bidder. - CERC (Grant of Connectivity, Long Term Access and Medium-term Access in Interstate Transmission and related matters) Regulation 2009 - CERC’s revised procedure for “Grant of Connectivity to Projects based on renewable sources to inter-state transmission system” - CEA (Technical Standards for Connectivity to Grid) Regulation,2007 - CEA (Technical Standards for construction of Electrical Plants and Electrical Lines) Regulation,2022 - CEA (Grid Standard) Regulation, 2010 - CEA (safety requirements for construction, operation and maintenance of Electrical Plants and Electrical Lines) Regulations,2011 - Central Electricity Authority (Measures relating to Safety and Electric Supply) Regulations, 2023 Dated 16-06-2023. - CEA (Installation and Operation of Meters) Regulations 2006 - Indian Electricity Grid Code Regulation,2023 - CEA (Technical standards for communication system in Power system operations) Regulation 2020 - CERC (Communication System for Inter State Transmission of Electricity) Regulations 2017 - MNRE guidelines/OM/Advisory/Clarifications - CEA (Cyber Security in Power Sector) Guidelines 2021 - POSOCO (Grid controller of India) / RLDC first time charging approval as amended time to time, including registration fees is in the scope of Bidder. - Draft detailed procedure covering modalities for first time energization and integration of new or modified power system element dated 25th August 2023 - Electrical inspector approval for charging of Solar generation plant and 33kV transmission lines up to PSS-2 including PTCC clearance if required. - GNA (General Network Access) Regulation 2022 and its amendments from time to time including drafts. - Guidelines for the validity period of type test(s) conducted on major electrical equipment as amended from time to time - Guidelines for Model Quality Assurance Plan (MQAP) for major equipment of Power sector. - Procedure for Grant of temporary General Network Access (T-GNA) to the inter state transmission system through national open access registry (NOAR) dated 29 september, 2023. - First time energization and integration (FTE&I) of new or modified power system element as per IEGC 2023. - FORMATs of Technical Data for Connection Agreement as per CERC (Connectivity and General Network Access to the inter-State Transmission System) Regulations, 2022. - Any other standards / regulations / draft regulations / rules / procedures / formats / requirements (explicit and/or implicit) etc. of concern competent statutory authorities. - Inverter and WMS shall be provided with Dual Master facility. - Bidder shall conduct and get approval for detailed Grid compliance studies with Power Plant Controllers up to POI as per CEA technical standard for grid connectivity and latest guidelines and practices of CTUIL / RLDC / POSOCO / NLDC for first charging clearance (written, verbal or practices followed by concern competent statutory authorities within stipulated timeline as given in the applicable regulations). Bidder to refer latest FTC (First Time Charging) procedures as applicable. The grid compliance studies to be done in PSS/E and PSCAD as per RLDC / POSOCO requirement. Bidder shall provide and get approval from respective authorities, all the technical details including but not limited to Inverter bench marking report, Generic model data of inverters, suitable for use in PSS/E and PSCAD software available at RLDC and Encrypted user-defined model (UDM) /generic model of inverter in suitable software format as per requirement of RLDC. In case any site testing required for grid compliance shall also be conducted by Bidder. - Bidder shall prepare and get approval from applicable authorities the detailed consolidated Grid compliance system studies as per GNA / CEA regulations during detail engineering up to 400kV substation of CTUIL and any other approvals for commissioning of 500 MW Solar Project. Bidder to check availability of PSSE and PSCAD model of Inverter and PPCs shall be ensured by Bidder during selection of respective Manufacturer(s). - The preliminary system study input parameters related to the PSS-2 (400/33kV, 1200MW) and 400kV transmission line between PSS-2 and KPS-II (CTUIL 400/765kV) substation are as under and all other details pertaining to PSS-2 and transmission line (PSS-2 to KPS-II) shall be provided to the successful Bidder during detail engineering stage. For each 340/170/170 MVA, 400/33/33 kV Power Transformer following parameters may be considered for preliminary system study. Impedances: - HV-LV1 & HV-LV2 = 15.0% +/- 7.5% tolerance (Base 170 MVA, at principal tap). - LV1-LV2 = 27% +/-15% tolerance. (Base 170 MVA, at principal tap). Note: For reactive power sizing, positive tolerance of above Impedances shall be considered and for fault level negative tolerance of above Impedances shall be considered. Losses: - No Load Loss at rated voltage and frequency = 135 KW - Load Loss at rated current and at 75°C for HV and LV. (LV1+LV2) windings, at principal tap position = 760 KW. - I2R Loss at rated current and at 75°C for HV and LV (LV1+LV2) windings, at principal tap position = 600 KW 400KV Transmission Line following parameters may be considered for preliminary system study: - 400KV S/C Transmission line on D/C Tower (Approx. 14.5KM) - Quad Moose equivalent AL59 Conductor - Any other parameters required for system study is to be arrange by the Bidder. - Bidder shall update themselves latest requirement for technical data requirement, PSSE and PSCAD generic Model as per RLDC / CTU etc. - All equipment, materials and services whether explicitly stated in Technical Specifications or otherwise and that are necessary for the successful commissioning of Solar Plant as per latest statutory regulations/procedures issued by bodies like CERC/SERC, CEA, WRLDC/SLDC, CTU/STU, MNRE, other Ministry /Authorities etc. shall be deemed to be included in the scope of work of the Bidder. |

# SCHEDULE-II PROJECT INFORMATION

- PROJECT INFORMATION

|  | Owner |  | : | GUJARAT INDUTRIES POWER COMPANY LIMITED. |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Consultant |  | : | TATA Consulting Engineers Limited 71 Cunningham Road, Bangalore – 560052 |  |  |
|  | Project title |  | : | 500MW AC Solar PV Plant at Khavda, Gujarat |  |  |
|  | Location |  | : | Khavda, Tal. Bhuj, Dist. Kutch, Gujarat. Land Coordinates: 24°3'16.03"N, 69°36'43.59"E |  |  |
|  | District |  | : | Kutch |  |  |
|  | Nearest Town |  | : | Bhuj (approx. 90km) |  |  |
|  | Nearest railway station |  | : | Bhuj (approx. 90km) |  |  |
|  | Nearest airport |  | : | Shyamji Krishna Verma Airport, Bhuj – approx.125km Kandla Airport – 190 Kms |  |  |
|  | Access road |  | : | Gujarat SH-45 (1km) |  |  |
|  | ### Wind data (as per IS: 875, part 3) |  |  |  |  |  |
|  |  | ### Basic wind speed |  |  | : | 47 m/s |
|  | Seismic data |  |  |  | : | As per IS: 1893 (latest revision) |
|  |  | Zone |  |  | : | 5 |
|  | Languages spoken in the region: |  |  |  | : | Guajarati, Hindi |
|  | Official language for the bidder to deal with |  |  |  | : | English |
|  | Installation of modules |  |  |  | : | Ground mounted |
|  | # ELECTRICAL |  |  |  |  |  |
|  | # Power evacuation |  |  |  |  |  |
|  | # From PV plant to RE PARK Pooling SUBSTATION-2 (400/33kV) |  |  |  | : | 400/33 kV |

- Project capacity

| Name of the Project | Development of 500MW (AC) Solar Photovoltaic Project (Phase-1) at 2375 MW RE PARK near village Khavda in the State of Gujarat, India. Sub plots: 1X300 and 1x200 MW AC |
| --- | --- |
| Plant Capacity | 500 MW AC / 625 MWp at Grid Connection Points (500 MW (AC)) – Total Blocks – 1x300MW (AC) and 1x200 MW (AC) PV Module shall be free issued to the Bidder by GIPCL |

- TECHNOLOGY

In Solar Photo Voltaic Power Generation, the direct conversion of solar radiation into electricity is achieved by using semiconductor devices “Solar Cells”, which work on the principles of photo electric effect. Technology proposed shall have  proven track record, long term past performance in India for similar scale of PV plants and site conditions.

- OTHER DETAILS

The following clearances shall be arranged by bidder. However, necessary documentations/ applications shall be in the name of GIPCL.

| SL | ITEM | DETAILS |
| --- | --- | --- |
| 1 | Water Requirement during construction | By bidder |
| 2 | Power Requirement during construction | By bidder |
| 3 | MNRE Clearance | To be facilitated by bidder |
| 4 | Chief Electrical Inspector Clearance | By bidder |
| 5 | Any other applicable clearance/approval required for commissioning and O&M of the plant | By bidder |

- SITE SPECIFIC TECHNICAL DATA

- SOLAR INSOLATION DATA FOR PROPOSED SITE

| Month | Solar Insolation (kWhr/m2) |
| --- | --- |
| January | 134.4 |
| February | 157.5 |
| March | 213.5 |
| April | 205.9 |
| May | 227.7 |
| June | 179.8 |
| July | 169.8 |
| August | 145.1 |
| September | 180.2 |
| October | 184.5 |
| November | 147.7 |
| December | 126.5 |
| Year | 2072.6 |

- MODULE MOUNTING – Single Axis E-W Tracker

- CABLE LAYING METHODOLOGY

- All cable within Solar generation plant boundary are to be laid above ground  and or underground keeping in view of the site-specific issues related to water submergence, soil condition etc, which shall be reviewed during the detail design engineering. Bidder may suggest alternate cable laying methodology which will be finalised during detail engineering. Bidder to ensure that the cables are laid properly in line with the design consideration adopted in sizing calculations and have to guarantee the cable performance and tolerance to the site conditions.

- The cables specifications / design shall be suitably selected as per philosophy / methodology of cable laying decided during detail engineering by the Bidder considering the site environmental conditions etc. Bidder shall submit the final specification with methodology for GIPCL Approval,.

However, methodology for all 33kV cables for 33KV Transmission lines (including spare 33kV cables) laying in Park area (in allocated corridor) shall be underground and or above ground.

Further, cable laying methodology and philosophy in allocated park cable corridor shall be as per Park Developer’s requirements (GIPCL).

- PROJECT LOCATION CLASSIFICATION (CORROSION PROTECTION)

  - Corrosive Category (Galvanization)

| Parameter | Corrosive Category (as per ISO12944-2) | Minimum Galvanized Thickness at any point of measurement and no averaging shall be allowed |
| --- | --- | --- |
| For below Ground Structures (including up to 300mm above ground) | C5-M | 110 Microns |
| For Above Ground Structures (Beyond 300mm) | C4 | 90 Microns |

  - Corrosive category (for Paints)

- Classification of environments for Corrosive category shall be in accordance with ISO12944, the applicable atmospheric corrosivity categories C5-M.

- ISO12944 shall be used related to paint systems in combination with guidance for the selection of different types of protective paint system.

- Wherever specification allows LT electrical panels, UPS, SCADA panel, Fire protection panel etc. associated with Inverter station to be placed outdoor, the enclosure of the same should be well engineered product having proper ventilation system and must be protected from harsh environment & direct sunlight/rainfall. Radiation and absorption effects of outdoor environment must be considered for temperature rise calculations. The temperature rise should not be more than working temperature of components. Suitable extended shed / canopy shall be provided for all outdoor equipment / devises.

- For metal enclosed outdoor, HT switchgear, pooling switchgear on the LT side (if applicable from string inverter to inverter transformer), suitable extended shed shall be provided considering the O&M space. O&M spaces requirement shall be finalised during detailed engineering as per Owner’s requirement without any financial implication to the Owner.

- Painting of outdoor metallic enclosed electrical panels including HT switchgear shall be as per ISO 12944-5, corresponding to minimum C5-M (very high marine) category.

- For outdoor inverter including containerized solution, painting corresponding to site condition shall be provided.

Unless specified otherwise, all steel structures exposed to environment would be painted to meet the requirements as mentioned in Clause no 5 (D) of Project information.

- SEISMIC DATA & DESIGN CRITERIA – Seismic Zone V, Provisions of IS 1893 (Part 1) shall be followed.

- WIND DATA & DESIGN CRITERIA

Basic wind speed shall be as per IS 875 (Part-3) (Based on survey of India Political map printed in 2002).

The minimum design wind pressure (Pd) to be considered for design of MMS, Equipment Fixing, Buildings, Rooms, etc. as below:

| BASIC WIND SPEED, m/s | Design Wind Pressure, min, Pd (N/m2) |
| --- | --- |
| 47 | 890 |

For Khavda park, the minimum design wind pressure (Pd) = 890 N/m2

- The requirement of Comprehensive AMC of Critical Equipment is revised as follows

| Equipment/System | Comprehensive AMC* |
| --- | --- |
| Inverter | 10 Years |
| SCADA | 10 Years |
| Tracker | 10 Years |

* Starts from date of commissioning of full capacity

## PROVENNESS CRITERIA

The vendor/ sub-vendor(s) who are not part of Approved vendor List is/are required to meet the Provenness criteria and/or qualification requirement for critical component and bought out item as per the criteria stipulated below:

- Tracker System:

The vendor should have designed, manufactured, supplied, erected/supervised erection, and commissioned/supervised commissioning Solar Tracker System of the proposed design/type of cumulative capacity of 40 MWp or above, out of which at least one such supply order for a single plant should be of 10 MWp or above capacity. The Vendor may use the credentials of its Parent/Group/Holding company for meeting the requirement. The reference plant in which 10 MWp or above capacity Solar Tracker System was supplied, must have been in successful operation for at least one (1) year prior to the following reference date:

Date of submission of Provenness documents to GIPCL or (LOA date + 6 months), whichever is earlier.

And

The proposed Tracker design/type shall be of proven technology with Independent Engineers Bankability review report from reputable agencies like Black and Veatch, DNV, IITs or other premier institutions/agencies.